## Contents
Workbook Contents
Click on tabs at the bottom of the screen to access the following:
Tab 1. Contents (current tab)
Tab 2. Aerated Grit Chamber Design
Tab 3. Estimation of Peaking Factor
Why you shouldn’t give copies of this workbook away
We at EngineeringExcelTemplates.com hope that you find this workbook useful. If you
would like us to develop additional useful spreadsheets for you in the future, then encourage
your friends and colleagues to buy their own copies, rather than allowing them to copy
the spreadsheet you purchased. We have deliberately set our prices so low that no one
can really claim that they can’t afford to pay. But low prices will work for us—that is, we
can stay in business—only if we can sell enough copies. Bottom line: the more you get
other people to pay for their own copies, the more low-cost useful spreadsheets will be
available for you in the future.
This workbook is provided "as is", without warranty of any kind, express or
implied.
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2014 Engineering Excel Templates. All Rights Reserved.

## Aerated Grit Chamber Design
Aerated Grit Chamber Design Calculations - S.I. units
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes | [8 empty] | Aerated Grit Chambers - Typical Parameter Values
Inputs |  |  |  |  | Calculations |  |  |  | Parameter | Range | Typical Value | Unit
Design Ave Flow Rate, Q = |  | 10500 | m3/d |  | Peak Hourly Flow Rate, Qp = | 34230 | m3/d |  | Detention time | 2 - 5 | 3 | min
(at peak hourly flow rate)
Peaking Factor, PF = |  | 3.26 |  |  | Grit Chamber Volume, V = | 71.3125 | m3 |  | Tank Depth | 2 - 5 |  | m
(Peak hourly flow/Average Flow) |  |  |  |  | (for each tank)
Tank Depth, D = |  | 2.5 | m |  | Tank Width, W = | 3.0836 | m |  | Tank Width | 2.5 - 7 |  | m
Length-Width Ratio , L:W = |  | 3 |  |  | Tank Length, L = | 9.2507 | m |  | Tank Depth | 7.5 - 20 |  | m
Design Detention Time
at Peak Flow Rate, t = |  | 3 | min | Width-Depth Ratio , W:D = |  | 1.2334 | m |  | Width:Depth ratio | 1:1 - 5:1 | 1.5:1
Air Supply per
Unit of Length , Qa/L = |  | 0.3 | m3/min-m |  | Required Air Supply , Qa = | 2.7752 | m3/min |  | Length:Width ratio | 3:1 - 5:1 | 4:1
(per tank)
Number of Grit Chambers = |  | 2 |  | Total Req. Air Supply , Qatot = |  | 5.5504 | m3/min |  | Required Air Supply | 0.2 - 0.5 |  | m3/min-m
(per unit of length)
NOTES: | 1. The next worksheet may be used to estimate the peaking factor based on the design
average flow rate. If you use that worksheet, enter the result in cell C9 above.
SOURCE: The information in this table came from Table 5-17, p 389 in:
2. Ranges and typical values for most of the user input parameters and some of
| the output calculated values, are given in the table at the right. | [6 empty] | Metcalf & Eddy, Wastewater Engineering Treatment and Reuse, 4th Ed, McGraw Hill, 2003,
3. If the calculated values of W, L, and/or W:D are not acceptable (within range), the
input value(s) of tank depth, Length:Width ratio, and/or number of grit chambers
should be changed.
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2014 Engineering Excel Templates. All Rights Reserved.

## Est. of Peaking Factor
Estimation of Peaking Factor - S.I. units
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
Inputs |  |  |  |  | Calculations
Design Ave Flow Rate, Q = |  | 10500 | m3/d |  | Peaking Factor, PF = | 3.2564
(Peak hourly flow/Average Flow)
NOTE: The peaking factor is calculated from the following equation:
PF = - 0.4343 Ln(Q) + 7.2776 |  |  |  | (Q is in m3/d)
SOURCE: This equation was derived using the graph shown at the right with data from:
Metcalf & Eddy, Wastewater Engineering Treatment and Reuse, 4th Ed, McGraw Hill, 2003,
Figure 3-13, p 202.
Find more Excel spreadsheets for engineering at
|  | EngineeringExcelTemplates.com | [6 empty] | Peaking
[7 empty] | Population | m3/d | Factor
[7 empty] | 5000 | 1892.705 | 4
[7 empty] | 10000 | 3785.41 | 3.7
| Copyright © 2014 Engineering Excel Templates. All Rights Reserved. | [5 empty] | 20000 | 7570.82 | 3.4
[7 empty] | 50000 | 18927.05 | 3
[7 empty] | 100000 | 37854.1 | 2.7
[7 empty] | 200000 | 75708.2 | 2.4
[7 empty] | 500000 | 189270.5 | 2
[7 empty] | 1000000 | 378541 | 1.7