## 1. Contents
Workbook Contents
Click on tabs at the bottom of the screen to access the following:
Tab 1. Contents (current tab)
Tab 2. General WW Information Input (Flow & concentrations)
Tab 3. Aeration Tank Sizing Calculations
Tab 4. Aeration Tank Operations Calculations
Tab 5. Oxygen Requirement/Blower Sizing Calculations
Why you shouldn’t give copies of this workbook away
We at EngineeringExcelTemplates.com hope that you find this workbook useful. If you
would like us to develop additional useful spreadsheets for you in the future, then encourage
your friends and colleagues to buy their own copies, rather than allowing them to copy
the spreadsheet you purchased. We have deliberately set our prices so low that no one
can really claim that they can’t afford to pay. But low prices will work for us—that is, we
can stay in business—only if we can sell enough copies. Bottom line: the more you get
other people to pay for their own copies, the more low-cost useful spreadsheets will be
available for you in the future.
This workbook is provided "as is", without warranty of any kind, express or
implied.
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2018 Harlan H. Bengtson. All Rights Reserved.

## 2. WW Info Input
Activated Sludge Waste Water Treatment Calculations - S.I. units
1. Input of General Parameter Values:
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
Inputs
Design ww Flow Rate, Qo = |  | 5678.1 | m3/d | Prim. Effl. TSS, Xo = | 180 | g/m3
Waste/recycle activated
Prim. Effl. BOD, So = |  | 160 | g/m3 | sludge SS conc., Xw = | 6800 | g/m3
Aeration tank MLSS, X = |  | 2100 | g/m3 | Secondary Effl. TSS, Xe = | 20 | g/m3
% volatile MLSS, %Vol = |  | 70%
NOTE: The above values will be used for these parameters in the other three worksheets.
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2018 Harlan H. Bengtson. All Rights Reserved.
Ref.: Bengtson, Harlan H., |  |  | Activated Sludge Calculations Spreadsheet: Aeration Tank Calculations
an Amazon Kindle ebook
Ref.: Bengtson, Harlan H., |  |  | Biological Wastewater Treatment Process Design Calculations
available as a paperback book and as an Amazon Kindle ebook

## 3. Tank Sizing Calcns
Activated Sludge Waste Water Treatment Calculations - S.I. units
2. Aeration Tank Sizing Calculations
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
A. Aeration Tank Design based on volumetric loading
Inputs |  |  | Calculations (based on Volumetric Loading)
Design Vol. Loading, VL = | 0.5606 |  | Aeration tank volume, V = | 1620.578 | m3
(kg BOD/day/m3)
Values Transferred from Worksheet 2: |  |  | Check on other design parameters:
Design ww Flow Rate, Qo = | 5678.1 | m3/d | Aeration tank HRT = | 6.8498 | hr
Prim. Effl. BOD, So = | 160 | g/m3 | Aeration tank F:M = | 0.38136
(kg BOD/day/kg MLVSS)
Aeration tank MLSS, X = | 2100 | g/m3
% volatile MLSS, %Vol = | 70%
Equations used for Calculations:
V = (So*Qo/1000)/VL | [5 empty] | Adapted from: Metcalf & Eddy, Inc, (Revised by Tchobanoglous, G, Burton, F.L., Stensel, H.D.,
Wastewater Engineering, Treatment and Reuse, 4th Ed., New York, NY, 2003.
HRT = 24*V/Qo
F:M = (So*Qo)/(%Vol*X*V) | [6 empty] | Find more Excel spreadsheets for engineering at:
EngineeringExcelTemplates.com
Copyright © 2018 Harlan H. Bengtson. All Rights Reserved.
B. Aeration Tank Design based on hydraulic loading
Inputs |  |  | Check on other design parameters: |  |  |  | Ref.: Bengtson, Harlan H., |  | Activated Sludge Calculations Spreadsheet: Aeration Tank Calculations
an Amazon Kindle ebook
Design Aer. tank HRT = | 7 | hr | Volumetric Loading, VL = | 0.54857
|  |  | (kg BOD/day/m3) |  |  |  | Ref.: Bengtson, Harlan H., |  | Biological Wastewater Treatment Process Design Calculations
Calculations (based on Hydraulic Loading) |  |  | Aeration tank F:M = | 0.37318 |  |  |  |  | available as a paperback book and as an Amazon Kindle ebook
(kg BOD/day/kg MLVSS)
Aeration tank volume, V = | 1656.1125 | m3
C. Aeration Tank Design based on F:M ratio
Inputs
Aeration tank F:M = | 0.35 |  | Check on other design parameters:
(kg BOD/day/kg MLVSS)
|  |  | Volumetric Loading, VL = | 0.5145
Calculations (based on F:M ratio) |  |  | (kg BOD/day/m3)
Aeration tank volume, V = | 1765.7843 | m3 | Aeration tank HRT = | 7.4636 | hr

## 4. Operations Calcns
Activated Sludge Waste Water Treatment Calculations - S.I. units
3. Aeration Tank Operation Calculations
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
Values Transferred from Worksheet 2: |  |  |  |  | Inputs
Design ww Flow Rate, Qo = |  | 5678.1 | m3/d |  | Aeration tank vol., V = | 1699 | m3
Prim. Effl. BOD, So = |  | 160 | g/m3 |  | Sludge ret. time, SRT = | 12 | days
Aeration tank MLSS, X = |  | 2100 | g/m3 |  | Calculations
% volatile MLSS, %Vol = |  | 70% |  |  | Aeration tank F:M = | 0.36376
Waste/recycle activated |  |  |  |  | (kg BOD/day/kg MLVSS)
sludge SS conc., Xw = |  | 6800 | g/m3 | Waste Act. Sludge Rate, Qw = |  | 27.024 | m3/d
Recycle Activated
Prim. Effl. TSS, Xo = |  | 180 | g/m3 |  | Sludge Flow Rate, Qr = | 2319.5643 | m3/d
Secondary Effl. TSS, Xe = |  | 20 | g/m3
Equations used for Calculations:
Qr = Qo(X - Xo)/(Xw - X)
Adapted from: Metcalf & Eddy, Inc, (Revised by Tchobanoglous, G, Burton, F.L., Stensel, H.D.,
Qw = (1/Xw)[(V*X/SRT) - QeXe] | [7 empty] | Wastewater Engineering, Treatment and Reuse, 4th Ed., New York, NY, 2003.
F:M = (So*Qo)/(%Vol*X*V) | [6 empty] | Ref.: Bengtson, Harlan H., |  |  | Activated Sludge Calculations Spreadsheet: Aeration Tank Calculations
an Amazon Kindle ebook
[7 empty] | Ref.: Bengtson, Harlan H., |  |  | Biological Wastewater Treatment Process Design Calculations
| Find more Excel spreadsheets for engineering at: | [7 empty] | available as a paperback book and as an Amazon Kindle ebook
EngineeringExcelTemplates.com
Copyright © 2018 Engineering Excel Templates. All Rights Reserved.

## 5. Oxygen_Blower Calcns
Activated Sludge Waste Water Treatment Calculations - S.I. units
4. Oxygen Requirement/Blower Sizing Calculations
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
Values Transferred from Previous Worksheets:
Design ww Flow Rate, Qo = |  | 5678.1 | m3/d |  | Prim. Effl. BOD, So = |  | 160 | g/m3
Additional User Inputs:
Rules of Thumb for Estimating Oxygen/Air Requirements for Coarse or Fine Bubble Diffusers
Influent TKN, TKNo = |  | 35 | g/m3 | Target Effl NH4-N conc, Ne = |  |  | 0.5 | g/m3
(needed only if nitrification is to be achieved) |  |  |  |  | (needed only if nitrification is to be achieved) |  |  |  | Source:
Target Effluent BOD, Se = |  | 20 | g/m3 | [5 empty] | http://www.xylemwatersolutions.com/scs/sweden/sv-se/produkter/cirkulationspumpar/documents/san3.pdf
A. Simplified Estimates Using "Rules of Thumb" - See Notes at Right | [8 empty] | 1. The typical AOR/SOR (or AOTE/SOTE) is 0.50 for a coarse bubble aertion system.
1. Inputs: (Values of "Rule of Thumb" Constants to be used in Calculations - See notes at right) | [8 empty] | 2. The typical AOR/SOR (or AOTE/SOTE) is 0.33 for a fine bubble aertion system.
O2 needed per kg BOD = |  | 1.2 | kg O2/kg BOD |  | Depth of Diffusers = |  | 3.66 | m | 3. The typical SOTE is 0.75% per foot (2.46%/m) of diffuser submergence for a coarse bubble system
O2 needed per kg NH3-N = |  | 4.57 | kg O2/kg NH3-N |  | Normal Temperature = |  | 0 | oC
SOTE as Function of Depth = |  | 6.56% | % per m depth |  | Normal Pressure = |  | 1 | bar | 4. The typical SOTE is 2.0% per foot (6.56%/m) of diffuser submergence for a fine bubble system
AOTE/SOTE = |  | 0.33 |  |  | Atmospheric Pressure = |  | 1.014 | bar
Press. Drop across Diffuser = |  | 0.03 | bar |  | Air Density at STP = |  | 1.275 | kg/m3 | 3. Air weighs 1.275 kg/m3 (at 0oC and 1 bar) and contains 23% oxygen by weight, thus:
(from mfr/vendor) |  |  |  |  | O2 Content in Air = |  | 0.293 | kg/m3
4. Air contains 0.293 kg of oxygen/m3.
2. Calculations for BOD Removal Only:
7. For biological treatment with SRT from 5 to 10 days, kg oxygen required /kg BOD removed
BOD Daily Loading = |  | 33.1223 | kg/hr |  |  | AOTE = | 7.923% |  | is typically in the range from 0.92 - 1.1 kg O2/kg BOD. Higher SRT results in a higher value
Oxygen Requirement = |  | 39.7467 | kg/hr |  | Air Requirement = |  | 1712.1215 | Nm3/hr | of kg O2 required/kg BOD removed.
| SOTE = | 24.01% |  |  | Blower Outlet Pressure = |  | 1.403 | bar
8. The oxidation of 1 kg of ammonia nitrogen typically requires 4.1 to 4.6 kg of oxygen.
3. Calculations for BOD Removal and Nitrification:
NH3-N Daily Loading = |  | 8.1623 | kg/hr |  |  | AOTE = | 7.923% |  | Activated Sludge Kinetic Coefficients for heterotrophic bacteria at 20oC (for BOD removal)
Oxygen Requirement = |  | 77.0483 | kg/hr |  | Air Requirement = |  | 3318.917 | Nm3/hr
| SOTE = | 24.01% |  |  | Blower Outlet Pressure = |  | 1.403 | bar | Coefficient |  | Unit |  | Range | Typical Value
[9 empty] | Y |  | g VSS/day/g bCOD |  | 0.30 - 0.50 | 0.4
B. More Detailed Estimates Using Biol. Kinetics and Diffuser Parameters | [8 empty] | kd |  | g VSS/day/g VSS |  | 0.06 - 0.20 | 0.12
1. Inputs (See tables at right for typical values of kinetic coefficients and oxygen transfer parameters.) | [8 empty] | fd |  | dimensionless |  | 0.08 - 0.20 | 0.15
q values for temperature corrections
Std O2 Transf. Effic., SOTE = |  | 20% |  |  | Ratio of BOD5/BODu, f = |  | 0.67 |  | for kd |  | dimensionless |  | 1.03 - 1.08 | 1.04
(from diffuser mfr or vendor) |  |  |  | D.O. conc to be maintained for WW
Design ww Temp., Tww = |  | 10 | oC |  | trtmt operation, CL = |  | 2 | g/m3 | Parameters used to calculate AOTE from SOTE
|  |  |  | Ratio of oxygen transfer rate in wastewater |  |  |  |  | Parameter |  | Range of Values |  | Typical Value | Units
Blower efficiency, h = |  | 70% |  | to that in clean water, a = |  |  | 0.5 |  | a (fine bubble) |  | 0.4 - 0.7 |  | 0.5 - 0.6 | dimensionless
|  |  |  | Ratio of D.O. saturation in wastewater to that |  |  |  |  | a (coarse bubble) |  | 0.6 - 0.95 |  | 0.7 - 0.8 | dimensionless
Rel. Humidity of Air, RHa = |  | 50% |  | in clean water at same T & P, B = |  |  | 1 |  | B |  | 0.95 - 0.99 |  |  | dimensionless
|  |  |  | D.O. saturation conc. For clean water |  |  |  |  | P |  | 0.9 - 1 |  |  | dimensionless
Design air Temperature, Ta = |  | 10 | oC | at ww temp. & 1 atm, Cs = |  |  | 11.28 | g/m3 | CL |  |  |  | 2 | mg/L
[9 empty] | F |  | 0.65 - 0.9 |  |  | dimensionless
Diffuser fouling factor, F = |  | 0.8 |  | Press. drop at blower inlet, DPin = |  |  | 0.021 | bar
|  |  |  | (due to filter, silencer, etc.) |  |  |  |  | Adapted from: Metcalf & Eddy, Inc, (Revised by Tchobanoglous, G, Burton, F.L., Stensel, H.D.,
Synthesis Yield Coeff, Y = |  | 0.6 | kgVSS/kg BOD5 |  | Peaking Factor, Fp = |  | 1.2 |  | Wastewater Engineering, Treatment and Reuse, 4th Ed., New York, NY, 2003.
Endog. Decay Coeff, kd20 = |  | 0.06 | kg VSS/d/kgVSS Peaking Factor, Fp = |  | Sludge ret. time, SRT = |  | 12 | days | and | http://www.xylemwatersolutions.com/scs/sweden/sv-se/produkter/cirkulationspumpar/documents/san3.pdf
(at 20 oC)
|  |  |  | Standard Rel. Humidity, RHs = |  |  | 36% |  | Equations used for these Calculations
2. Calculations for BOD Removal Only: | [8 empty] | Temperature correction for kd: kd at temp. T = (kd at 20oC)1.024(T - 20) ( T is in oC )
Endog. Decay Coeff, kdT = |  | 0.047332 | kgVSS/d/kg VSS |  | Design Air Density, rair = |  | 1.2478 | kg/m3 | Observed Yield (with recycle): Yobs = Y/(1 + kd*SRT)
(at ww temperature)
Observed Yield, Yobs = |  | 0.38266 | kg VSS/kgBOD5 |  | Required O2 flow rate = |  | 31.4384 | kg/hr | Required O2 Flow Rate (BOD removal only): kg/day O2 =(Qo*(So - Se)/1000)[(1/f) - 1.42 Yobs]
(with recycle)
Press. at mid depth, PD = |  | 1.1935 | bar |  | Required air flow rate = |  | 1383.4454 | m3/hr | Required O2 Flow Rate (BOD removal & Nitrification):
kg/day O2 = (Qo/1000){(So - Se)[1/f - 1.42 Yobs] + 4.57(TKNo - Ne)}
Act. O2 Transf. Effic., AOTE = |  | 7.889% |  | Design Act. Air Flow Rate, Am3/m = |  |  | 1660.1345 | m3/hr |  |  | NOTE: With nitrification, Se is typically taken to be zero because of the long SRT used.
(with peaking factor)
Vapor Press at Ta, PVa = |  | 0.01222 | bar | Des. Norm. Air Flow Rate, Nm3/m = |  |  | 1593.7702 | Nm3/hr | Actual O2 transfer effic. = AOTE = SOTE*a*F*[(B*(PD/Pstd)*Cs -CL)/Css]1.024(T-20)
[5 empty] | (with peaking factor) | [5 empty] | (Css = saturation D.O. in water at 20oC & 1 atm = 9.17 mg/L)
Vapor Press at TN, PVN = |  | 0.0060603 | bar |  | Blower outlet press, PB2 = |  | 1.4029 | bar
See descriptions of the parameters in the User Entry section above left.
3. Calculations for BOD Removal and Nitrification: | [8 empty] | Des. Actual Air Flow Rate: Am3/m = (kg/hr O2/AOTE)*MWair/[O2 fract in air)(MWO2)(rair)(60 min/hr)]
Required O2 flow rate = |  | 68.74 | kg/hr | Design Act. Air Flow Rate, Am3/m = |  |  | 3629.8783 | m3/hr | Des. Normal Air Flow Rate: Nm3/m = Am3/m(TN/Ta)(Pa/Pb){[Pb - (RHa*PVa)]/[PN - (RHN*PVN)]}
(with peaking factor)
Required air flow rate = |  | 3024.8986 | m3/hr | Des. Norm. Air Flow Rate, Nm3/m = |  |  | 3349.2154 | Nm3/hr | ( T is abs temp., P is abs press., RH is relative humidity, PV is vapor press., Pb is barometric press., subscript a is for
[5 empty] | (with peaking factor) |  |  |  | actual conditions and subscript N is for normal conditions.)
|  |  |  | Blower outlet pressure, PB2 = |  |  | 1.4029 | bar
Blower outlet pressure: PB2 = Patm + DPdiff + gH2O*ddiff
Reference: Bengtson, Harlan H., |  |  | Activated Sludge Calculations Spreadsheet: Aeration Tank Calculations
an Amazon Kindle ebook
[9 empty] | Reference for Antoine Eqn: |  |  | Perry's Chemical Engineers' Handbook, 8th Ed. - Table 13.4
Reference: Bengtson, Harlan H., |  |  | Biological Wastewater Treatment Process Design Calculations
|  | available as a paperback book and as an Amazon Kindle ebook | [6 empty] | Reference: Metcalf & Eddy, Inc, (Revised by Tchobanoglous, G, Burton, F.L., Stensel, H.D.,
Wastewater Engineering, Treatment and Reuse, 4th Ed., New York, NY, 2003.
Find more Excel spreadsheets for engineering at:
EngineeringExcelTemplates.com
Copyright © 2018 Harlan H. Bengtson. All Rights Reserved.