## 1. Contents
Workbook Contents
Click on tabs at the bottom of the screen to access the following:
Tab 1. Contents (current tab)
Tab 2. Sludge Quantity Calculations
Tab 3. Digester Tank Design Calculations
Why you shouldn’t give copies of this workbook away
We at EngineeringExcelTemplates.com hope that you find this workbook useful. If you
would like us to develop additional useful spreadsheets for you in the future, then encourage
your friends and colleagues to buy their own copies, rather than allowing them to copy
the spreadsheet you purchased. We have deliberately set our prices so low that no one
can really claim that they can’t afford to pay. But low prices will work for us—that is, we
can stay in business—only if we can sell enough copies. Bottom line: the more you get
other people to pay for their own copies, the more low-cost useful spreadsheets will be
available for you in the future.
This workbook is provided "as is", without warranty of any kind, express or
implied.
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2012 Engineering Excel Templates. All Rights Reserved.

## 2. Sludge Quant. Calcns
Anaerobic Digester Calculations - S.I. units
1. Sludge Quantity Calculations
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
Primary Sludge
Inputs |  |  | Inputs
Design Ave. Flow Rate, Qi = | 21600 | m3/d | Prim. Sludge solids conc. = | 5%
Peaking factor for
peak monthly flow, PF = | 1.2 |  | Prim. Sludge Sp. Grav. = | 1.02
Influent TSS, TSSi = | 400 | g/m3 | Prim. Clarif. % TSS rem = | 70%
After grit removal, TSSp = | 360 | g/m3
Calculations
Peak monthly flow, Qm = | 25920 | m3/d | TSS in Primary Sludge = | 6531.84 | kg/d
(used for design)
|  |  | Vol. Flow of Prim. Sludge = | 128.0753 | m3/d |  | Equations Used for Calculations
Waste Activated Sludge | [6 empty] | Peak monthly flow = (Design ave. flow rate)(Peaking factor) [ Qm = Qi*PF ]
Inputs |  |  | Calculations |  |  |  | kg/day of TSS in Prim. Sludge = Qm*TSSp*(Prim. Clarif. % TSS removal)/1000
Infl. BOD conc., BODi = | 375 | g/m3 | BOD to aeration tank = | 6512.4 | kg/d |  | Vol. Flow of Prim. Sldge = (lb/day of TSS in Prim. Sldge)/[1000*(Prim. Sldge solids conc.)(Sp. Gr.)
Prim. Clarif. % BOD rem = | 33% |  | Aeration tank volume, V = | 8140.5 | m3 |  | kg/day of BOD to aer. tank = (Peak mnthly flow)(BODi)(1 - % BOD rem. in prim. clarif.)/1000
Aeration tank MLSS, X = | 3500 | g/m3 |  |  |  |  | Aer. tank vol. in m3 = V = (kg/day of BOD to aer. tank)/VL
Waste Activated Sludge
Design SRT = | 13 | days | TSS flow rate, mdotWAS = | 1673.2731 | kg/d |  | kg/day of TSS in WAS, mdotWAS = VMG*X/(Design SRT*1000) - Qm*TSSe/1000
Design vol. loading |  |  | Waste Activated Sludge
for aeration tank, VL = | 0.8 |  | Flow Rate, Qw = | 167.3273 | m3/d |  | Waste Activated Sludge Flow Rate, Qw = mdotWAS*1000/TSSw
(kg BOD/day/m3)
WAS conc., TSSW = | 10000 | g/m3
Effl. TSS conc., TSSe = | 20 | g/m3
Thickened Waste Activated Sludge
Inputs |  |  | Calculations
Conc. Of thickened sludge = | 5% |  | TSS flow (thknd. Sludge) = | 1505.9458 | kg/d |  | lb/day of TSS in thickened sludge = (mdotWAS)(assumed solids recovery %)
Assumed solids recovery = | 90% |  | Flow rate (thknd. Sludge) = | 30.1189 | m3/d |  | MGD of thickened sludge = (lb/day of TSS in thcknd sldge)/[(conc. of thcknd sldge)(8.34)(106)
Reference: Mecalf & Eddy, Inc, Wastewater Engineering Treatment and Reuse, 4th Ed, revised by:
Tchobanoglous, G., Burton, F.L., and Stensel, D.H., McGraw Hill, 2003.

## 3. Design Calcns
Anaerobic Digester Calculations - S.I. units | [7 empty] | Typical Design Loading Rates for mesophilic, high-rate, complete mix Anaerobic Digesters
(from Metcalf & Eddy reference below)
2. Single Stage, Mesophilic, Completely Mixed Digester Design | [7 empty] | Solids Loading Rate: 1.6 - 4.8 kg VSS/day/m3
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes | [7 empty] | Solids Retention Time: 15 - 20 days
Volume Determination | [7 empty] | Typically based on peak 2 week or peak monthly influent wastewater flow rate
Choose Design Criterion (either Solids Loading Rate or Solids Retention Time)
by entering either yes or no in the blue cell below: | [7 empty] | Equations Used for Calculations
Solids Loading Rate | no |  |  | Solids Retention Time | yes |  |  | kg/day of VSS to digester = (kg/day TSS in prim. sldge)(% vol. solids in prim. sldge)
(kg VSS/day/m3) |  |  |  | (SRT, days) | [5 empty] | + (kg/day of thcknd WAS)(% vol. solids in WAS)
Inputs |  |  |  | Calculations |  |  |  | For Solids Loading Rate as design criterion:
% Volatile solids in
primary sludge = | 70% |  | VSS flow rate to digester = |  | 5777.0446 | kg/d |  | Digester liquid volume in m3 = (kg/day of VSS to digester)/Solids Loading Rate
% Volatile solids in
waste activated sludge = | 80% |  | Total digester liquid volume = |  | 3544.8312 | m3 |  | For Solids Retention Time as design criterion:
Solids Retention Time = | 12 | days |  | Solids Loading Rate = | 1.6297 |  |  | Digester liquid volume in m3
|  |  |  | (kg VSS/day/cu.m.) |  |  |  | = (flow rate of prim. sldge + flow rate of thcknd WAS)(Solids Retention Time)
(Note that solids retention time = liquid retention time for a completely mixed reactor)
Tank Dimensions
Number of tanks = | 2 |  |  | Liquid volume/digester = | 1772.4156 | m3 |  | Liquid volume/digester = (Total digester liquid volume)/(Number of tanks)
Side water depth = | 10 | m |  | Diameter of digester = | 15.0223 | m |  | Diameter of digester = [(liquid volume/digester)*4/p*SWD]0.5
(min SWD = 7.5 m; max SWD = 15 m) |  |  |  | (min diam = 6 m; max diam = 38 m)
Reference: Mecalf & Eddy, Inc, Wastewater Engineering Treatment and Reuse, 4th Ed, revised by:
Tchobanoglous, G., Burton, F.L., and Stensel, D.H., McGraw Hill, 2003.