## 1. Contents
Workbook Contents
Click on tabs at the bottom of the screen to access the following:
Tab 1. Contents (current tab)
Tab 2. Secondary Clarifier Design Calculations
Tab 3. Primary Clarifier Design Calculations
Why you shouldn’t give copies of this workbook away
We at EngineeringExcelTemplates.com hope that you find this workbook useful. If you
would like us to develop additional useful spreadsheets for you in the future, then encourage
your friends and colleagues to buy their own copies, rather than allowing them to copy
the spreadsheet you purchased. We have deliberately set our prices so low that no one
can really claim that they can’t afford to pay. But low prices will work for us—that is, we
can stay in business—only if we can sell enough copies. Bottom line: the more you get
other people to pay for their own copies, the more low-cost useful spreadsheets will be
available for you in the future.
This workbook is provided "as is", without warranty of any kind, express or
implied.
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2011 Engineering Excel Templates. All Rights Reserved.

## 2. Sec Clarifier Design
Activated Sludge Waste Water Treatment Calculations - S.I. units
2. Secondary Clarifier Design
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
Inputs |  |  |  |  | Calculations
Prim. Effl. Flow Rate, Q = |  | 10600 | m3/d |  | Recycle Act. Sl. Rate, Qr = | 3180 | m3/d
Return Act. Sl. Ratio, R = |  | 0.3 |  |  | Peak Hourly Flow Rate, Qp = | 23850 | m3/d
Aeration tank MLSS, X = |  | 2100 | mg/L |  | Calculate Clarifier Area based on SOR
Design Surface |  |  |  |  | Based on ave. Flow: A1 = | 481.8182 | m2
Overflow Rate , SOR = |  | 22 | m3/d/m2 | (ave) | Based on Peak Flow: A2 = | 507.4468 | m2
|  | 47 | m3/d/m2 | (peak) | The larger of the two areas is: | 507.4468 | m2
Design Solids
Loading Rate , SLR = |  | 5 | kg/hr/m2 | (ave) | Calculate Clarifier Area based on SLR
|  | 8 | kg/hr/m2 | (peak) | Based on ave. Flow: A3 = | 241.15 | m2
[5 empty] | Based on Peak Flow: A4 = | 339.1172 | m2
Peaking Factor, PF = |  | 2.25 |  |  | The larger of the two areas is: | 339.1172 | m2
(for peak hourly flow)
[5 empty] | Area needed for Clarifier, A = | 507.4468 | m2
[5 empty] | (The largest of A1, A2, A3, & A4) |  |  | Adapted from: Metcalf & Eddy, Inc, (Revised by Tchobanoglous, G, Burton, F.L., Stensel, H.D.,
Wastewater Engineering, Treatment and Reuse, 4th Ed., New York, NY, 2003.
Calculate Circular Clarifier Diameter:
NOTE: The design parameters for a particular project will typically come from the design guide
Number of Clarifiers, N = |  | 2 |  |  | Clarifier Diameter, D = | 17.9736 | m | of the appropriate state, county or municipality.
Effluent Weir Calculations (Circular Clarifiers) | [8 empty] | Typical maximum values for Weir Overflow Rate (WOR):
Min. Diameter for single
Max Weir Overflow Rate = |  | 375 | m3/d/m |  | circular effluent weir = | 4.4988 | m |  | for Q < 3800 m3/day: |  |  | WOR < 250 m3/d/m
[5 empty] | Min. Diameter for circular Channel with |  |  |  | for Q > 3800 m3/day: |  |  | WOR < 375 m3/d/m
[5 empty] | effluent weir on each side = | 2.2494 | m
Typical Values for Peaking Factors (hourly maximum/daily average)
Calculate Length and Width for Rectangular Clarifier:
[10 empty] | Ave Flow, MGD | Peaking Factor
Number of Clarifiers, N = |  | 2 |  |  | Clarifier Width, W = | 7.9643 | m
Length/Width ratio, L/W = |  | 4 |  |  | Clarifier Length, L = | 15.9287 | m |  |  | < 0.1 | 3
[10 empty] | 0.1 - 0.3 | 2.9
Effluent Weir Calculations (Rectangular Clarifiers) | [9 empty] | 0.3 - 0.5 | 2.8
[5 empty] | Number of channel widths |  |  |  |  | 0.5 - 0.7 | 2.7
Max Weir Overflow Rate = |  | 375 | m3/d/m |  | needed for effluent weir = | 1.7746 |  |  |  | 0.7 - 1.0 | 2.6
[10 empty] | 1 - 2 | 2.5
[10 empty] | 2 - 4 | 2.25
Equations used for Calculations: |  |  |  |  | A note on unit conversions: |  |  |  |  | > 4 | 2
Clarifier area: A = Q/SOR |  |  |  |  | 1 mg/L = 0.001 kg/m3
Clarifier Area: A = (Q + Qr)*X*0.001/24*SLR
Effl. Weir Length: L = Q/WOR
Find more Excel spreadsheets for engineering at:
EngineeringExcelTemplates.com
Copyright © 2011 Engineering Excel Templates. All Rights Reserved.

## 3. Prim Clarif Design
Activated Sludge Waste Water Treatment Calculations - U.S. units
3. Primary Clarifier Design
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
Inputs |  |  |  | Calculations
Influent Flow Rate, Q = |  | 10600 | m3/d | Recycle Act. Sl. Rate, Qr = | 3180 | m3/d
Return Act. Sl. Ratio, R = |  | 0.3 |  | Peak Hourly Flow Rate, Qp = | 23850 | m3/d
Design Surface Overflow |  |  |  | Calculate Clarifier Area based on SOR
Rate (average) , SORa = |  | 40 | m3/d/m2
|  |  |  | Based on ave. Flow: A1 = | 265 | m2
Design Surface Overflow
Rate (peak) , SORp = |  | 100 | m3/d/m2 | Based on Peak Flow: A2 = | 238.5 | m2
Peaking Factor, PF = |  | 2.25 |  | The larger of the two areas is: | 265 | m2
(for peak hourly flow)
Calculate Circular Clarifier Diameter:
Number of Clarifiers, N = |  | 2 |  | Clarifier Diameter, D = | 12.9886 | m
Effluent Weir Calculations (Circular Clarifiers)
Min. Diameter for single
|  |  |  | circular effluent weir = | 8.4352 | m
Max Weir Overflow
Rate, WOR = |  | 200 | m3/hr/m | Min. Diameter for circular Channel with
|  |  |  | effluent weir on each side = | 4.2176 | m
Calculate Length and Width for Rectangular Clarifier: | [6 empty] | Adapted from: Metcalf & Eddy, Inc, (Revised by Tchobanoglous, G, Burton, F.L., Stensel, H.D.,
Wastewater Engineering, Treatment and Reuse, 4th Ed., New York, NY, 2003.
Number of Clarifiers, N = |  | 2 |  | Clarifier Width, W = | 5.7554 | m
Length/Width ratio, L/W = |  | 4 |  | Clarifier Length, L = | 11.5109 | m | NOTE: The design parameters for a particular project will typically come from the design guide
of the appropriate state, county or municipality.
Effluent Weir Calculations (Rectangular Clarifiers)
Max Weir Overflow |  |  |  | Number of channel widths
Rate, WOR = |  | 200 | m3/hr/m | needed for effluent weir = | 4.6043
| Equations used for Calculations: | [6 empty] | Typical Values for Peaking Factors (hourly maximum/daily average)
| Clarifier area: A = Q/SOR | [7 empty] | Ave Flow, MGD | Peaking Factor
| Effl. Weir Length: L = Q/WOR | [7 empty] | < 0.1 | 3
[9 empty] | 0.1 - 0.3 | 2.9
[9 empty] | 0.3 - 0.5 | 2.8
[9 empty] | 0.5 - 0.7 | 2.7
[9 empty] | 0.7 - 1.0 | 2.6
| Find more Excel spreadsheets for engineering at: | [7 empty] | 1 - 2 | 2.5
|  | EngineeringExcelTemplates.com | [6 empty] | 2 - 4 | 2.25
[9 empty] | > 4 | 2
Copyright © 2011 Engineering Excel Templates. All Rights Reserved.