## 1. Contents
Workbook Contents
NOTE: The calculations in this workbook follows the steps used in Example 8-9 in:
Click on tabs at the bottom of the screen to access the following:
Metcalf & Eddy, Inc, (Revised by Tchobanoglous, G, Burton, F.L., Stensel, H.D.),
| Tab 1. Contents (current tab) |  |  |  | Wastewater Engineering, Treatment and Reuse, 4th Ed., New York, NY, 2003.
Tab 2. CMAS - Tertiary Anoxic Denitrification
Why you shouldn’t give copies of this workbook away
We at EngineeringExcelTemplates.com hope that you find this workbook useful. If you
would like us to develop additional useful spreadsheets for you in the future, then encourage
your friends and colleagues to buy their own copies, rather than allowing them to copy
the spreadsheet you purchased. We have deliberately set our prices so low that no one
can really claim that they can’t afford to pay. But low prices will work for us—that is, we
can stay in business—only if we can sell enough copies. Bottom line: the more you get
other people to pay for their own copies, the more low-cost useful spreadsheets will be
available for you in the future.
This workbook is provided "as is", without warranty of any kind, express or
implied.
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2015 Harlan H. Bengtson. All Rights Reserved.

## 2. CMAS - Tertiary Denitrif.
Completely Mixed Activated Sludge Denitrification Calculations - S.I. units
Tertiary Denitrification
This spreadsheet makes the design calculations for a postanoxic, tertiary denitrification basin
to follow a treatment process that produces a nitrified effluent that serves as influent to this process.
process as shown in the diagram at the right.
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
User Inputs 1 - Wastewater Parameters
Design ww Flow Rate, Qo = |  | 4000 | m3/d |  | Anoxic Tank Temp., Tww = | 15 | oC
Influent TSS, TSSo = |  | 20 | mg/L | Target Effl. nitrate conc. Ne = |  | 2 | mg/L
Influent NO3-N, NO3-No = |  | 25 | mg/L | Resid. biomass fract., fd = |  | 0.15
Est. Effl. TSS, TSSe = |  | 15 | mg/L | Waste/recycle A.S. conc. TSSw = |  | 6500 | mg/L
User Inputs 2 - Design Parameters
Mixing energy
Design SRT, SRT = |  | 5 | days |  | for anoxic reactor = | 10 | kW/103 m3
Tank Freeboard = |  | 0.5 | m |  | Design MLSS, MLSS = | 2000 | mg/L
Number of Tanks = |  | 3 |  |  | Reaer. Det. Time, treaer = | 15 | min
Liquid Depth in Tank = |  | 5 | m |  | Tank L:W ratio = | 1
(target L:W - only used if tank is rectangular)
User Inputs 3 - Kinetic Coefficients for Denitrification with Methanol
[5 empty] | at 10oC | at 20oC
Synth. Yield Coeff, YD (g VSS/g bCOD) = |  |  |  |  | 0.17 | 0.18
Half Veloc. Coeff., KsD (mg/L) = |  |  |  |  | 12.6 | 9.1
Max spec. grwth rate, mmD (gVSS/d/gVSS) = |  |  |  |  | 0.52 | 1.86
Endog. decay coeff., kdD (g VSS/d/g VSS) = |  |  |  |  | 0.04 | 0.05
Max spec. substrate util. rate, k (g VSS/d/g VSS) = |  |  |  |  | 3.1 | 10.3 |  | Equations used for the calculations: (note that conversion factors are needed in some of the equations)
Calculations - Postanoxic basin design for denitrification | [8 empty] | S = Ks[1 + (kd)SRT]/[SRT(mm - kd) - 1
1. Calculate kinetic coefficients at ww temperature, Tww (by interpolation) | [8 empty] | Yn = Y/[1 + (kd)SRT]
Endog. decay coeff., kdD = |  | 0.045 | g VSS/d/g VSS |  | Synth. Yield Coeff, YD = | 0.175 | g VSS/g bCOD |  | bCOD/NO4-N = 2.86/(1 - 1.42Yn)
Max spec. substr. Utiliz., k = |  | 6.7 | g VSS/d/g VSS |  | Half Veloc. Coeff., KsD = | 10.85 | mg/L
Methanol dose (as COD) = (bCOD/NO4-N)(NOx - Ne)
2. Calculate Methanol Requirement | [8 empty] | Methanol dose = Methanol dose (as COD)/(1.5 g COD/g methanol)
Resid. Meth. Conc in effl., S: |  | 2.866 | mg/L |  | Methanol dose (as COD) = | 85.5339 | mg/L COD |  | Daily Methanol needed = 8.34 (Methanol dose in mg/L)Q
| Yn = | 0.14286 | g VSS/g bCOD |  | Methanol dose = | 57.0226 | mg/L CH3OH
bCOD/NO4-N = |  | 3.5943 | g/g |  | Daily Methanol needed = | 228.0904 | kg/d
3. Calculate Anoxic Tank Volume, Dimensions and Detention Time
(User Input needed in the Blue Cells)
Solids prod. rate, PX,TSS = |  | 139442.4675 | kg/d | Min. Anoxic Tank Volume, Van = |  | 348.6062 | m3
Click on green box and then on
Min. Vol. per tank, Vtank = |  | 116.2021 | m3 | arrow to Select Tank Shape: |  | rectangular
Calculated Tank Width = |  | 4.8208 | m | Actual Tank Width: |  | 5 | m
Calculated Tank Length = |  | 4.8208 | m | Actual Tank Length: |  | 5 | m
Tank Wall Height = |  | 5.5 | m | Actual Tank liquid Volume = |  | 125 | m3
Anoxic Det'n time, t = |  | 2.25 | hr |  | Anoxic Tank Mixing Power = | 3.75 | kW
4. Calculate Reaeration Volume, and Dimensions
(User Input is needed in the Blue Cells. The shape is kept the same as the anoxic tank(s).)
Reaertion Volume, Vreaer = |  | 41.6667 | m3 | Min. Reaer. Vol/tank, Vtank = |  | 13.8889 | m3
Tank Width = |  | 5 | m | Actual Tank Width: |  | 5 | m
Calculated Tank Length = |  | 0.55556 | m | Actual Tank Length: |  | 0.7 | m
Tank Wall Height = |  | 5.5 | m | Actual Tank liquid Volume = |  | 17.5 | m3
Anoxic Det'n time, t = |  | 18.9 | min
5. Calculate Sludge Recycle Rate and Sludge Wasting Rate | [7 empty] | Qr = Qo(MLSS - TSSo)/(TSSw - MLSS)
A.S. Recycle Rate, Qr = |  | 1760 | m3/d |  | Waste A.S. Rate, Qw2 = | 13.8782 | m3/d | Qw = [(V*MLSS/SRT) - QoTSSe]/(TSSw - TSSe)
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2015 Harlan H. Bengtson. All Rights Reserved.