## 1. Contents
Workbook Contents
NOTE: The calculations in these worksheets follow the steps used in Examples 8-3, 8-7, 8-10 and 8-13 in:
Click on tabs at the bottom of the screen to access the following:
Metcalf & Eddy/Aecom, Wastewater Engineering Treatment and Resource Recovery,
| Tab 1. Contents (current tab) |  |  |  | 5th Ed., McGraw-Hill, 20014.
Tab 2. User Inputs and Constants
Tab 3. CMAS - Nitrification (and BOD Removal)
Tab 4. CMAS - Pre-Anoxic Denitrification
Tab 5. A2O EBPR Process
Tab 6. CMAS - Post-Anoxic Denitrification
Tab 7. rbCOD/P vs VFA/rbCOD Equation
Why you shouldn’t give copies of this workbook away
We at EngineeringExcelTemplates.com hope that you find this workbook useful. If you
would like us to develop additional useful spreadsheets for you in the future, then encourage
your friends and colleagues to buy their own copies, rather than allowing them to copy
the spreadsheet you purchased. We have deliberately set our prices so low that no one
can really claim that they can’t afford to pay. But low prices will work for us—that is, we
can stay in business—only if we can sell enough copies. Bottom line: the more you get
other people to pay for their own copies, the more low-cost useful spreadsheets will be
available for you in the future.
This workbook is provided "as is", without warranty of any kind, express or
implied.
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2020 Harlan H. Bengtson. All Rights Reserved.

## 2. User Inputs and Constants
Completely Mixed Activated Sludge Design Calculations - S.I. units | [8 empty] | Activated Sludge Kinetic Coefficients for heterotrophic bacteria at 20oC (for BOD removal)
User Inputs
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes | [9 empty] | Coefficient | Unit | Typical Value | Range*
User Inputs - Wastewater Parameters/Characteristics | [9 empty] | mm | kg VSS/day/kg VSS | 6 | 3.0 - 13.2
Design ww Flow Rate, Qo = |  | 4000 | m3/d |  | Prim. Effl. TSS, TSSo = |  | 70 | mg/L |  | Ks | mg/L bCOD | 8 | 5.0 - 40.0
[5 empty] | Prim. Effl. VSS, VSSo = |  | 60 | mg/L
Prim. Effl. BOD, BODo = |  | 160 | mg/L | [6 empty] | Y | kg VSS/day/kg bCOD | 0.45 | 0.30 - 0.50
sBOD, sBODo = |  | 70 | mg/L |  | Prim. Effl. Acetate, VFAo = |  | 15 | mg/L
[5 empty] | Prim. Effl. TKN, TKNo = |  | 35 | mg/L |  | kd | kg VSS/day/kg VSS | 0.12 | 0.06 - 0.20
Prim. Effl. COD, CODo = |  | 300 | mg/L | TKN peak/ave factor , FS = |  |  | 1.5
sCOD, sCODo = |  | 132 | mg/L | Prim. Effl. NH4-N, NH4-No = |  |  | 25 | mg/L |  | fd | dimensionless | 0.15 | 0.08 - 0.20
rbCOD, rbCODo = |  | 75 | mg/L | Prim. Effl. Tot. Phos, TPo = |  |  | 6 | mg/L |  |  |  | * Range of values is from M&E 4th Ed
q values for temperature corrections
ratio, bCOD/BOD = |  | 1.6 |  | Prim. Effl. Alkalinity, Alko = |  |  | 140 | mg/L as CaCO3
[10 empty] | for mm | dimensionless | 1.07 | 1.03 - 1.08
SRT for BOD Rem., SRT = |  | 5 | days |  | Design MLSS,, XTSS = |  | 2000 | mg/L |  | for kd | dimensionless | 1.04 | 1.03 - 1.08
Aeration WW Temp., Tww = |  | 12 | oC |  |  | to | 3000 | mg/L |  | for Ks | dimensionless | 1 | 1
User Inputs - Biological Kinetic Coefficients |  |  |  |  | (See typical values at right) |  |  |  |  | From Table 8-14, Metcalf & Eddy/Aecom, Wastewater Engineering Treatment
and Resource Recovery, 5th Ed., McGraw-Hill, 20014.
1. For BOD Removal: |  |  |  | Resid. biomass fract., fd = |  |  | 0.15
Synth. Yield Coeff, Y = |  | 0.45 | g VSS/g bCOD |  | Half Veloc. Coeff., Ks = |  | 8 | mg/L |  | Activated Sludge Nitrification Kinetic Coefficients at 20oC
Temp coeff, q, for mm = |  | 1.07 | Max spec. grwth rate at 20oC, mm20 = |  |  |  | 6 | g VSS/d/g VSS
Temp coeff, q, for kd = |  | 1.04 | Endog. decay coeff. at 20oC, kd20 = |  |  |  | 0.12 | g VSS/d/g VSS |  | Coefficient | Unit | Typical Value | Range*
2. For Nitrification: | [9 empty] | mmn | kg VSS/day/kg VSS | 0.9 | 0.2 - 0.90
Synth. Yield Coeff, Yn = |  | 0.15 | g VSS/g NOx
Temp coeff, q, for mmn = |  | 1.072 | Max spec. grwth rate at 20oC, mmn20 = |  |  |  | 0.9 | g VSS/d/g VSS |  | Kn | mg/L NH4-N | 0.5 | 0.50 - 1.0
Temp coeff, q, for kdn = |  | 1.029 | Endog. decay coeff. at 20oC, kdn20 = |  |  |  | 0.17 | g VSS/d/g VSS
Temp coeff, q, for Ksn = |  | 1 | Half Veloc. Coeff. At 20oC, Ksn = |  |  |  | 0.5 | mg/L |  | Yn | kg VSS/kg NH4-N | 0.15 | 0.10 - 0.15
Constants Used in the Calculations | [9 empty] | kdn | kg VSS/day/kg VSS | 0.17 | 0.05 - 0.15
Ratio of BOD5 to BODu, f = |  | 0.67 | BODu equiv. of VSS = |  |  | 1.42 | g BODu/g VSS |  |  | Ko | mg/L | 0.5 | 0.40 - 0.60
* Range of values is from M&E 4th Ed
q values for temperature corrections
[10 empty] | for mmn | dimensionless | 1.072 | 1.06 - 1.123
[10 empty] | for kdn | dimensionless | 1.029 | 1.03 - 1.08
[10 empty] | for Kn | dimensionless | 1 | 1.03 - 1.123
| Find more Excel spreadsheets for engineering at | [8 empty] | From Table 8-14, Metcalf & Eddy/Aecom, Wastewater Engineering Treatment
|  |  | EngineeringExcelTemplates.com | [6 empty] | and Resource Recovery, 5th Ed., McGraw-Hill, 20014.
Copyright © 2020 Harlan H. Bengtson. All Rights Reserved.

## 3. CMAS - Nitrification
Completely Mixed Activated Sludge Nitrification Calculations - S.I. units
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
User Inputs |  |  |  |  | Design MLSS, = |  | 3000 | mg/L
Target effluent concentrations: |  |  |  |  | Prim. Effl. TKN, TKNo = |  | 35 | mg/L
| BODe = | 15 | mg/L |  | Initial Estimate of NOx = |  | 28.1767 | mg/L
| TSSe = | 15 | mg/L | Waste/recycle A.S. conc. TSSw = |  |  | 6500 | mg/L
| NH4-Ne = | 0.5 | mg/L |  | Liquid Depth in Tank = |  | 5 | m
Tank Freeboard = |  | 0.5 | m |  | Tank L:W ratio = |  | 1
Number of Aeration Tanks = |  | 3 |  | (target L:W - only used if tank is rectangular)
NOTE: An initial estimate is needed for NOx in cell H7 to start an iterative calculation of
NOx below. 80% of the primary effluent TKN is suggested for this initial estimate.
Calculations - Reator design for BOD Removal and Nitrification
1. Calculate Design SRT
mmn at Tww = |  | 0.51604 | g VSS/d/g VSS |  | Ksn at Tww = |  | 0 | mg/L | Equations used for the calculations: (note that conversion factors are needed in some of the equations)
kdn at Tww = |  | 0 | g VSS/d/g VSS |  |  | mn = | 0.41283 | g VSS/d/g VSS
Theoretical SRT = |  | 2.4223 | days |  | Design SRT, SRT = |  | 3.6334 | days |  | mnm at Tww = mnm,20 qTww - 20 |  | Kn at Tww = Kn,20 qTww - 20
2. Calculate the Biomass Production Rate | [9 empty] | kdn at Tww = kdn,20 qTww - 20 | (Tww must be in oC for these calculations)
mm at Tww = |  | 0 | g VSS/d/g VSS |  | kd at Tww = |  | 0 | g VSS/d/g VSS
| bCODo = | 256 | mg/L |  |  | S = | -8 | mg bCOD/L |  | mn = [ mnmN/(Kn + N) ] [ DO/(Ko + DO) ] |  | Theroetical SRT = 1/mn
Biomass Production Rate, PX,bio = |  |  | 492.106 | kg VSS/day | [5 empty] | Design SRT = (FS)(Theoretical SRT) FS = TKNpeak/TKNaverage
3. Determine the Amount of Nitrogen Oxidized to Nitrate | [9 empty] | PX,bio = QY(So - S)/(1 + kdSRT) + fdkdQY(So - S)SRT/(1 + kdSRT) + QYn(NOx)/(1 + kdnSRT)
Calculated amount of nitrogen oxidized to nitrate, NOx = |  |  |  |  | 19.7368 | mg/L |  |  |  | S = Ks[1 + (kd)SRT]/[SRT(mm - kd) - 1
Difference between estimated and calculated values for NOx = | [5 empty] | 8.4399 | mg/L |  |  | NOx = TKN - Ne - 0.12PX,bio/Q
Goal Seek Result:
Amount of nitrogen oxidized to nitrate, NOx = |  |  |  | Redo Goal Seek |  | mg/L |  |  |  | PX,VSS = PX,bio + Q(nbVSS) | PX,TSS = PX,VSS + Q(TSSo - VSSo)
NOTE: This is an iterative solution. You must use Excel's "Goal Seek" to find the NOx value as
follows: Place the cursor on cell G31 and click on "goal seek" (in the "tools" menu of older versions
and under "Data What If Analysis" in newer versions of Excel). Enter values to "Set cell:" G31, "To
value:" 0, "By changing cell:" H7, and click on "OK". The calculated value of NOx will appear in cell
G33 and cell G31 should be zero if the process worked properly. Note that cell H7 needs an initial
estimate for NOx in order for the iterative solution to work properly.
4. Determine the Production Rate and Mass of VSS and TSS in the Aeration Basin | [9 empty] | V = Mass of MLSS/MLSS
bpCOD/pCOD = |  | 0.85714 |  |  | nbVSS = | 8.5714 | mg/L |  |  | Mass of MLVSS = (PX,VSS) SRT
Aeration Tank VSS Production Rate, PX,VSS = |  |  |  |  | 526.3917 | kg VSS/day |  |  |  | Mass of MLSS = (PX,TSS) SRT
Aeration Tank TSS Production Rate, PX,TSS = |  |  |  |  | 653.234 | kg TSS/day
Mass of MLVSS = |  | 1912.6086 | kg VSS |  | Mass of MLSS = |  | 2373.4812 | kg TSS
5. Calculate Aeration Tank Volume and dimensions, Detention Time, and MLVSS
(User Input needed in Blue Cells)
Req. Aeration Vol., Vaer = |  | 791.1604 | m3 | Click on green box and then on | [5 empty] | detention time: t = V/Q
Req. Vol. per tank, Vtank = |  | 263.7201 | m3 | arrow to Select Tank Shape: |  |  | rectangular
Calculated Tank Width = |  | 7.2625 | m | Actual Tank Width: |  |  | 12.5 | m |  | F/M = QSo/XV
Calculated Tank Length = |  | 7.2625 | m | Actual Tank Length: |  |  | 12.5 | m
Tank Wall Height = |  | 5.5 | m | Actual Tank liquid Volume = |  |  | 781.25 | m3 |  | Vol BOD loading = QSo/V
Aeration Det'n time, t = |  | 14.0625 | hr |  | MLVSS, = |  | 2417.4726 | mg/L
6. Calculate F/M and Volumetric BOD Loading
F/M = | 0.33462 | g BOD/d/g MLVSS |  |  | Vol. BOD Loading = |  | 0.80894 | kg BOD/d/m3
7. Calculate Sludge Recycle Rate and Sludge Wasting Rate
A.S. Recycle Rate, Qr = |  | 3348.5714 | m3/d |  | Waste A.S. Rate, Qw = |  | 289.1525 | m3/d |  | Qr = Qo(MLSS - TSSo)/(TSSw - MLSS)
Qw = [(V*MLSS/SRT) - QoTSSe]/(TSSw - TSSe)
8. Oxygen/Air Requirement and Blower Calculations
A. Simplified Estimates using "Rules of Thumb" shown at right
Rules of Thumb for Estimating Oxygen/Air Requirements for Coarse or Fine Bubble Diffusers
i) INPUTS (Values of "Rule of Thumb" Constants for the Calculations) | [8 empty] | Source:
http://www.xylemwatersolutions.com/scs/sweden/sv-se/produkter/cirkulationspumpar/documents/san3.pdf
O2 needed per kg BOD = |  | 1.3 | kg O2/kg BOD |  | Depth of Diffusers = |  | 4.4 | m
O2 needed per kg NH4-N = |  | 4.57 | kg O2/kg NH4-N |  | Normal Temperature = |  | 0 | oC | 1. The typical AOR/SOR (or AOTE/SOTE) is 0.50 for a coarse bubble aertion system.
SOTE as Function of Depth = |  | 6.56% | % per m depth |  | Normal Pressure = |  | 1 | bar | 2. The typical AOR/SOR (or AOTE/SOTE) is 0.33 for a fine bubble aertion system.
AOTE/SOTE = |  | 0.33 |  |  | Atmospheric Pressure = |  | 1.014 | bar | 3. The typical SOTE is 0.75% per foot (2.46%/m) of diffuser submergence for a coarse bubble system
Press. Drop across Diffuser = |  | 0.03 | bar |  | Air Density at STP = |  | 1.275 | kg/m3 | 4. The typical SOTE is 2.0% per foot (6.56%/m) of diffuser submergence for a fine bubble system
(from mfr/vendor) |  |  |  |  | O2 Content in Air = |  | 0.293 | kg/m3 | 5. Air weighs 1.275 kg/m3 (at 0oC and 1 bar) and contains 23% oxygen by weight, thus:
6. Air contains 0.2930 kg of oxygen/m3.
ii) Calculations | [8 empty] | 7. For biological treatment with SRT from 5 to 10 days, kg oxygen required /kg BOD removed
Press. at mid depth, PD = |  | 1.2298 | bar |  | NH3-N Daily Loading = |  | 4.0833 | kg/hr | is typically in the range from 0.92 - 1.1 kg O2/kg BOD. Higher SRT results in a higher value
BOD Daily Loading = |  | 24.1667 | kg/hr |  |  | AOTE = | 9.525% |  | of kg O2 required/kg BOD removed.
Oxygen Requirement = |  | 50.0775 | kg/hr |  | Air Requirement = |  | 1794.3393 | Nm3/hr | 8. The oxidation of 1 kg of ammonia nitrogen typically requires 4.1 to 4.6 kg of oxygen.
| SOTE = | 28.86% |  |  | Blower Outlet Pressure = |  | 1.4756 | bar
B. More Detailed Estimates using Biological Kinetics and Diffuser Parameters
i) INPUTS
Std O2 Transf. Effic., SOTE = |  | 29% |  | Ratio of oxygen transfer rate in wastewater |  |  |  |  | See derivation of equation for Saturated D.O. vs Tempreature at 1 atm on Worksheet 3.
(from diffuser mfr or vendor) |  |  |  | to that in clean water, a = |  |  | 0.65
Diffuser fouling factor, F = |  | 0.9 |  | Ratio of saturated D.O. in wastewater to that in |  |  |  |  | Oxygen demand = Ro = Q(So - S) - 1.42PX,bio + 4.33Q(NOx)
Sat'n DO at 20oC, 1 atm, Css = |  | 9.08 | mg/L | clean water at same T & P, b = |  |  | 0.95
| D.O. conc. To be maintained for WW trtmt operation, CL = | [5 empty] | 2 | mg/L | AOTE = SOTE*a*F*[(B*(PD/Pstd)*Cs -CL)/Css]q(Tww-20)
ii) Calculations
Sat'n DO at Tww, 1 atm, Cs = |  | 10.7727 | mg/L |  | Press. at mid depth, PD = |  | 1.2298 | bar | Alkalinity to be added = Influent Alk - Alk used + Alk residual desired
Observed Yield, Yobs = |  | 0.45 | kg VSS/kg BOD5 |  | O2 Utilization Rate = |  | 48.5406 | kg/hr
Effl. Soluble BOD, sBODe = |  | 3.5001 | mg/L | Des. Air Flow Rate, Nm3/hr: |  |  | 1212.3874 | Nm3/hr | Alkalinity used for nitrification = (7.14 g CaCO3/g NH3-N) NOx
Actual O2 Transfer |  |  |  | Des. Air Flow Rate, m3/hr: |  |  | 857.6956 | m3/hr
Efficiency, AOTE = |  | 14.45% |  |  | Blower Outlet Pressure = |  | 1.4756 | bar | Alk needed as sodium bicarbonate = Alk needed as CaCO3(84/50)
9. Calculate Alkalinity Requirement
Alk. used for nitrification = |  | 140.9209 | mg/L as CaCO3 |  | Resid. Alk. to maintain: |  | 80 | mg/L as CaCO3
(User Entered Value)
Alkalinity needed = |  | 80.9209 | mg/L as CaCO3 |  | Alkalinity needed = |  | 323.6836 | kg/day as CaCO3
Sodium bicarbonate needed per day to maintain alkalinity = | [5 empty] | 543.7884 | kg/day NaHCO3
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2020 Harlan H Bengtson. All Rights Reserved.
cylindrical
rectangular

## 4. CMAS - Pre-Anoxic Denitrif.
Completely Mixed Activated Sludge Denitrification Calculations - S.I. units
PreAnoxic Denitrification
This spreadsheet makes the design calculations for a preanoxic denitrification basin to go
with the CMAS system designed for BOD removal and Nitrification in Worksheet 3.
(The wastewater parameters/characteristics and biological kinetic coefficients entered on
Worksheet 2 will also be used in this worksheet.)
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
Inputs - Additional Design Parameters |  |  |  |  | Mixing energy
[5 empty] | for anoxic reactor = |  | 10 | kW/103 m3
Nitrate conc. in RAS = |  | 6 | mg/L |  | RAS ratio = |  | 0.5
Effl. nitrate conc. Ne = |  | 6 | mg/L |  | Design % Excess
Temp. Coeff for SDNR = |  | 1.026 |  |  | Nitrif. Capacity = |  | 20%
Prelim. est. of det. Time, tan: |  | 1.8951 | hr |  | Liquid Depth in Tank = |  | 5 | m
Tank Freeboard = |  | 0.5 | m |  | Tank L:W ratio = |  | 1 |  | Equations used for the calculations: (note that conversion factors are needed in some of the equations)
Number of Tanks = |  | 3 |  | (target L:W - only used if tank is rectangular)
NOTE: A preliminary estimate for anoxic detention time is needed in cell C14 to start an | [9 empty] | Active biomass conc: Xb = [ Q(SRT)/V ][ Y(So - S)/(1 + kd(SRT) ]
iterative calculation of minimum anoxic detention time below. | [9 empty] | Internal Recycle Ratio: IR = (NOx/Ne) - 1.0 - R
Calculations - Preanoxic basin design for denitrification
Flow rate to anoxic tank: Qanox = IR(Q) + R(Q)
1. Calculate active biomass concentration and IR ratio | [9 empty] | NOx feed rate = (Qanox)(NOXRAS)
Active biomass conc., Xb = |  | 2116.2402 | mg/L |  | IR ratio, IR = |  | 1.7895
Anoxic volume: Vanox = t Qo ( t = estimated detention time )
2. Calculate feed rate of NO4-N to anoxic tank and anoxic tank volume
F/M = QSo/XV
Flow rate to anoxic tank = |  | 9157.8798 | m3/d |  | NOX rate to anoxic tank = |  | 54947.2789 | g/day
(flow containing nitrate) |  |  |  |  | Anoxic tank volume, Van = |  | 315.8422 | m3 |  | Rate at which NO3-N can be reduced: NOr = Vanox(SDNR)(MLVSS)
(based on detention time value in cell C15)
3. Calculate the F/M ratio | [9 empty] | Coefficients for SDNR Equation
Anoxic tank F/M ratio = |  | 0.95751 | g BOD/d/g MLVSS | [6 empty] | rbCOD/bCOD | bo | b1
4. Calculate the SDNR |  |  |  |  | (User Entered Values Needed Here) |  |  |  |  | 0.1 | 0.186 | 0.078
[10 empty] | 0.2 | 0.213 | 0.118
rbCOD/bCOD ratio = |  | 0.29297 | Next lower rbCOD/bCOD value from table: |  |  |  |  | 0.2 |  | 0.3 | 0.235 | 0.141
|  |  | Next higher rbCOD/bCOD value from table: |  |  |  |  | 0.3 |  | 0.4 | 0.242 | 0.152
[10 empty] | 0.5 | 0.27 | 0.162
SDNR for rbCOD/bCOD = |  | 0.2 | is equal to: |  | 0.20788
SDNR for rbCOD/bCOD = |  | 0.3 | is equal to: |  | 0.22888 |  |  |  |  | 0.2 | 0.213 | 0.118
[10 empty] | 0.3 | 0.235 | 0.141
SDNR for rbCOD/bCOD = |  | 0.29297 | is equal to: |  | 0.2274 | g NO3-N/day/g biomass (at 20oC)
Equations for SDNR as a function of F/M
at Tww, SDNR = |  | 0.18519 | g NO3-N/day/g biomass (at Tww)
For F/M < 0.5, SDNR = 0.24*F/M (at 20oC)
Value of SDNR including Internal Recycle correction:
For F/M > 0.5, SDNR = bo + b1[ ln(F/M) ] (at 20oC)
For IR = 2, SDNR = |  | 0.10791
For IR = 3, SDNR = |  | 0.17445 | [7 empty] | Temperature Correction: |  | SDNR at Tww = (SDNR at 20oC)(1.026Tww - 20)
|  |  | For IR = | 1.7895 | SDNR = | 0.12418 |  |  |  | Equations for Internal Recycle Correction:
5. Calculate the Anoxic Tank Volume, Dimensions and Detention Time | [9 empty] | for IR < 1, no correction is needed
(User Input needed in Blue Cells)
for IR = 2, SDNRadj = SDNRIR1 - 0.0166LN(F/M) - 0.078
NO3-N reduction capacity = |  | 123779.8765 | g/d |  | % Excess Nitrif. Capacity: |  | 125.3%
Difference between Design and Calculated % Excess Nitrification Capacity = | [6 empty] | -1.0527 |  |  | for 3 < IR < 4, SDNRadj = SDNRIR1 - 0.029LN(F/M) - 0.012
Goal Seek Result:
Anoxic Tank min. Vol., Van = |  | Redo Goal Seek |  | m3 | min. Anox. Det. Time, tan = |  | #VALUE! | hr |  | NOTE: These equations are from:
Metcalf & Eddy/Aecom, (Revised by Tchobanoglous, G, Burton, F.L., Stensel, H.D.),
NOTE: This is an iterative solution. You must use Excel's "Goal Seek" to find the Van vand tan | [9 empty] | Wastewater Engineering, Treatment and Resource Recovery, 5th Ed., New York, NY, 2014.
values as follows: Place the cursor on cell H49 and click on "goal seek" (in the "tools" menu of
older versions and under "Data What If Analysis" in newer versions of Excel). Enter values to
"Set cell" H49 "To value:" 0, "By changing cell:" C14, and click on "OK". The calculated values
of Van and tan will be in cells C51 and H51. Cell H49 should be zero if the process worked properly.
A preliminary estimate for tan is needed in cell C14 in order for the iterative solution to work.
Click on green box and then on
Min. Vol. per tank, Vtank = |  | #VALUE! | m3 | arrow to Select Tank Shape: |  |  | rectangular
Calculated Tank Width = |  | #VALUE! | m | Actual Tank Width: |  |  | 5 | m
Calculated Tank Length = |  | #VALUE! | m | Actual Tank Length: |  |  | 5 | m
Tank Wall Height = |  | 5.5 | m | Actual Tank liquid Volume = |  |  | 125 | m3
Anoxic Det'n time, t = |  | 2.25 | hr
6. Recalculate the oxygen/air requirement due to the nitrate reduction oxygen credit
Oxygen credit = |  | 157.1492 | kg/day = |  | 6.5479 | kg/hr
O2 Utilization Rate = |  | 41.9927 | kg/hr | Req'd air flow rate, Nm3/hr = |  |  | 1048.8424 | Nm3/hr
|  |  |  | Req'd air flow rate, m3/hr = |  |  | 741.9967 | m3/hr
[5 empty] | Blower Outlet Pressure = |  | 1.4756 | bar |  | Oxygen credit for nitrate reduction = 2.86 Qo(NOx - Ne)
7. Recalculate Alkalinity Requirement
Alkalinity produced = |  | 49.0404 | mg/L as CaCO3 | [6 empty] | Alkalinity produced by nitrate reduction = 3.57(NOx - Ne)
Alkalinity needed = |  | 31.8804 | mg/L as CaCO3 |  | Alkalinity needed = |  | 127.5218 | kg/day as CaCO3
Sodium bicarbonate needed per day to maintain alkalinity = | [5 empty] | 214.2366 | kg/day NaHCO3
8. Calculate Anoxic tank mixing power needed
Anoxic Tank Mixing Power = |  | 3.75 | kW
9. Calculate Sludge Wasting Rate
Waste A.S. Rate, Qw = |  | 322.8323 | m3/d
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2020 Harlan H Bengtson. All Rights Reserved.
cylindrical
rectangular

## 5. A2O EBPR Process
Completely Mixed Activated Sludge Denitrification Calculations - S.I. units
PreAnoxic Denitrification - A2O EBPR Process
This spreadsheet makes the design calculations for enhanced biological phosphorus removal
with the CMAS system designed for preanoxic denitrification in Worksheet 4.
(The wastewater parameters/characteristics and biological kinetic coefficients entered on
Worksheet 2 will also be used in this worksheet.)
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
Inputs - Additional Design Parameters
Nitrate conc. in RAS = |  | 6 | mg/L |  | rbCOD used by nitrate = | 5.2 | g rbCOD/g NO3-N
Effl. nitrate conc. Ne = |  | 6 | mg/L |  | RAS ratio = | 0.6
Influent nbVSS, nbVSSo = |  | 20 | mg/L |  | Liquid Depth in Tank = | 5 | m
Anaerobic HRT = |  | 0.75 | hr |  | Tank L:W ratio = | 1 |  | Equations used for the calculations: (note that conversion factors are needed in some of the equations)
Tank Freeboard = |  | 0.5 | m | (target L:W - only used if tank is rectangular)
Number of Tanks = |  | 3 | [6 empty] | rbCOD in Influent = Qo*rbCODo
Calculations - Enhanced Biological Phosporus Removal by A2O Process | [8 empty] | NO3-N fed to Anaerobic Tank = RASRatio*Qo*(g rbCOD/d NO3-N)
1. Calculate the rbCOD available for Enhanced Biological Phosporus Removal | [8 empty] | rbCOD consumed by nitrate = (rbCOD used by nitrate)*(NO3-N fed to Anaerobic Tank)
rbCOD in Infl., rbCODo = |  | 300000 | g/d |  | NO3-N fed to
rbCOD consumed |  |  |  |  | Anaerobic Tank = | 12000 | g NO3-N/d |  | rbCOD available = rbCODo - rbCOD consumed by nitrate
| by nitrate = | 62400 | g rbCOD/d |  | rbCOD available = | 237600 | g rbCOD/d
2. Determine Phosporus Removal by EBPR | [8 empty] | Influent VFA/rbCOD ratio = VFAo/rbCODo
Infl. VFA/rbCOD ratio = |  | 0.2 |  |  | rbCOD/P removal = | 15.3488 | g rbCOD/g P |  | rbCOD/P = -65.53(VFA/rbCOD)3 + 125.22(VFA/rbCOD)2 - 82.644(VFA/rbCOD) + 27.393
*
P removal rate by EBPR = |  | 15480.0779 | g P/d | P conc. reduction by EBPR = |  | 3.87 | mg/L |  | P removal rate by EBPR = (rbCOD available)/(rbCOD/P removal)
P Conc. reduction by EBPR = removal rate by EBPR/Qo
3. Determine P Removal by other heterotrophic bacteria for synthesis
PX,bio (from Wksht 3) = |  | 492.106 | kg VSS/day |  | PX,bio (in g VSS/d) = | 492106.0092 | g VSS/day |  | PX,bio = QY(So - S)/(1 + kdSRT) + fdkdQY(So - S)SRT/(1 + kdSRT) + QYn(NOx)/(1 + kdnSRT)
P removal by Synthesis = |  | 7381.5901 | g P/day |  | Reduction in P Conc. = | 1.8454 | mg/L |  | P removal by Synthesis = 0.015*PX,bio (in g P/day)
4. Calculate Effluent P Concentration | [8 empty] | Reduction in P conc. = 0.015*PX,bio/Qo
Effluent P Conc., Pe = |  | 0.28458 | mg/L | [5 empty] | Effluent P Conc., Pe = Po - P conc. reduction by EBPR
- reduction of P conc. by other heterotrophic bacteria for synthesis
5. Calculate the Anoxic Tank Volume, Dimensions and Detention Time
Click on green box and then on
Min. Vol. per tank, Vtank = |  | 41.6667 | m3 | arrow to Select Tank Shape: |  | rectangular |  |  | Vtank = (Qo/N)*HRT
Calculated Tank Width = |  | 2.8868 | m | Actual Tank Width: |  | 3 | m
Calculated Tank Length = |  | 2.8868 | m | Actual Tank Length: |  | 3 | m
Tank Wall Height = |  | 5.5 | m | Actual Tank liquid Volume = |  | 45 | m3
Anoxic Det'n time, t = |  | 0.81 | hr
5. Calculate P Concentration in Waste Sludge | [8 empty] | Tot. Sludge Prod. Rate = (PX,bio/0.85) + (Qo*nbVSSo) + Qo*(TSSo - VSSo)
Total Sludge Producrion = |  | 698948.2461 | g/d |  | P Removal Rate = | 22861.668 | g/d |  | P Removal Rate = Qo(Po - Pe)
% P in waste sludge = |  | 3.271% | [6 empty] | % P in waste sludge = (P Removal Rate/Total Sludge Prod. Rate)*100%
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2020 Harlan H Bengtson. All Rights Reserved.

## 6. CMAS - Post-Anoxic Denitrif.
Completely Mixed Activated Sludge Denitrification Calculations - S.I. units
PostAnoxic, Two Sludge Denitrification
This spreadsheet makes the design calculations for a postanoxic, denitrification basin to go with
the CMAS system designed for BOD removal and Nitrification in Worksheet 3, as shown in the
diagram at the right. (The wastewater parameters/characteristics and some biological kinetic
coefficients entered on Worksheet 2 will also be used in this worksheet.)
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
Inputs - Additional Design Parameters
Mixing energy
Design MLSS, MLSSD2 = |  | 2000 | mg/L |  | for anoxic reactor = | 10 | kW/103 m3
Reaer. Det. Time, treaer = |  | 15 | min |  | Design SRT, SRTD2 = | 5 | days
Tank Freeboard = |  | 0.5 | m | Target Effl. nitrate conc. Ne = |  | 2 | mg/L
Number of Tanks = |  | 3 |  |  | Tank L:W ratio = | 1
Liquid Depth in Tank = |  | 5 | m | (target L:W - only used if tank is rectangular)
Est. Effl. TSS, TSSe = |  | 15 | mg/L | Waste/recycle A.S. conc. TSSw = |  | 6500 | mg/L
User Inputs - Kinetic Coefficients for Denitrification with Methanol
[5 empty] | at 10oC | at 20oC
Synth. Yield Coeff, YD (g VSS/g bCOD) = |  |  |  |  | 0.17 | 0.18
Half Veloc. Coeff., KsD (mg/L) = |  |  |  |  | 12.6 | 9.1
Max spec. grwth rate, mmD (gVSS/d/gVSS) = |  |  |  |  | 0.52 | 1.86
Endog. decay coeff., kdD (g VSS/d/g VSS) = |  |  |  |  | 0.04 | 0.05
Max spec. substrate util. rate, k (g VSS/d/g VSS) = |  |  |  |  | 3.1 | 10.3
Calculations - Postanoxic basin design for denitrification
1. Calculate kinetic coefficients at ww temperature, Tww (by interpolation)
Synth. Yield Coeff, YD = |  | 0.172 | g VSS/g bCOD |  | From wksht 2, Tww = | 12 | oC | Equations used for the calculations: (note that conversion factors are needed in some of the equations)
Endog. decay coeff., kdD = |  | 0.042 | g VSS/d/g VSS |  | Half Veloc. Coeff., KsD = | 11.9 | mg/L
Max spec. substr. Utiliz., k = |  | 4.54 | g VSS/d/g VSS | [5 empty] | S = Ks[1 + (kd)SRT]/[SRT(mm - kd) - 1
2. Calculate Methanol Requirement | [8 empty] | Yn = Y/[1 + (kd)SRT]
Resid. Meth. Conc in effl., S: |  | 5.344 | mg/L |  | Methanol dose (as COD) = | 69.0136 | mg/L COD |  | bCOD/NO4-N = 2.86/(1 - 1.42Yn)
| Yn = | 0.14215 | g VSS/g bCOD |  | Methanol dose = | 46.0091 | mg/L CH3OH
bCOD/NO4-N = |  | 3.5897 | g/g |  | Daily Methanol needed = | 184.0364 | kg/d |  | Methanol dose (as COD) = (bCOD/NO4-N)(NOx - Ne)
Methanol dose = Methanol dose (as COD)/(1.5 g COD/g methanol)
3. Calculate Anoxic Tank Volume, Dimensions and Detention Time
| (User Input needed in the Blue Cells) | [7 empty] | Daily Methanol needed = (Methanol dose in mg/L)Qo/(1000 g/kg)
Solids prod. rate, PX,TSS = |  | 107619.884 | g/d | Min. Anoxic Tank Volume, Van = |  | 269.0497 | m3
Click on green box and then on
Min. Vol. per tank, Vtank = |  | 89.6832 | m3 | arrow to Select Tank Shape: |  | rectangular
Calculated Tank Width = |  | 4.2352 | m | Actual Tank Width: |  | 5 | m
Calculated Tank Length = |  | 4.2352 | m | Actual Tank Length: |  | 5 | m
Tank Wall Height = |  | 5.5 | m | Actual Tank liquid Volume = |  | 125 | m3
Anoxic Det'n time, t = |  | 2.25 | hr |  | Anoxic Tank Mixing Power = | 3.75 | kW
4. Calculate Reaeration Volume, and Dimensions
(User Input is needed in the Blue Cells. The shape is kept the same as the anoxic tank(s).)
Reaertion Volume, Vreaer = |  | 41.6667 | m3 | Min. Reaer. Vol/tank, Vtank = |  | 13.8889 | m3
Tank Width = |  | 5 | m | Actual Tank Width: |  | 11 | m
Calculated Tank Length = |  | 0.55556 | m | Actual Tank Length: |  | 1.5 | m
Tank Wall Height = |  | 5.5 | m | Actual Tank liquid Volume = |  | 82.5 | m3
Anoxic Det'n time, t = |  | 89.1 | min
5. Calculate Sludge Recycle Rate and Sludge Wasting Rate
A.S. Recycle Rate, R2 = |  | 1715.5556 | m3/d
Waste A.S. Rate, Qw2 = |  | 13.8782 | m3/d
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2020 Harlan H Bengtson. All Rights Reserved.

## 7, rbCOD_P vs VFA_rbCOD
VFA/rbCOD | rbCOD/P
0.1 | 20.5
0.2 | 15
0.3 | 12
0.4 | 10.5
0.5 | 9.4 | rbCOD/P = -65.53(VFA/rbCOD)3 + 125.22(VFA/rbCOD)2 - 82.644(VFA/rbCOD) + 27.393
0.6 | 8.5
0.7 | 8.25
0.8 | 8
Source of data for this graph: Metcalf & Eddy, Wastewater Engineering Treatment and Resource Recovery, 5th Ed, 2014, Figure 8-38
Copyright © 2020 Harlan H Bengtson. All Rights Reserved.