## 1. Introduction
|  | Workbook Contents |  | Introduction to the MBBR worksheets in this workbook:
Click on tabs at the bottom of the screen to access the following: |  |  |  | Two worksheets are provided to carry out basin sizing and aeration calculations as well as
alkalinity requirements for a Pre-Anoxic Denitrification process and for a Post-Anoxic
| Tab 1. Introduction (current tab) |  |  | Denitrification process. The worksheets include calculations for the BOD removal stage
and nitrification stage as well as for the anoxic tank.
Tab 2. Pre-Anoxic Denitrification
Basin sizing is based on a carrier surface area loading rate (SALR). For BOD removal and
| Tab 3. Post-Anoxic Denitrification |  |  | denitrification, the design SALR value is selected by the user based on the treatment
objective, (e.g. high rate BOD removal, normal rate BOD removal, or low rate BOD removal.
| Tab 4. Derivation of Saturation DO vs T Equation |  |  | Typical SALR values are provided on the worksheets. For nitrification, the design SALR is
calculated from a kinetic model based on the D.O. level to be maintained in the reactor
and the target effluent ammonia nitrogen concentration.
Why you shouldn’t give copies of this workbook away
We at EngineeringExcelTemplates.com hope that you find this workbook useful. If you |  |  |  | Note that the estimated effluent concentration for BOD, or nitrate nitrogen from each
would like us to develop additional useful spreadsheets for you in the future, then encourage |  |  |  | BOD removal or denitrification stage is calculated by using an estimated value for the
your friends and colleagues to buy their own copies, rather than allowing them to copy |  |  |  | SARR/SALR (surface area removal rate/surface area loading rate). The estimated value
the spreadsheet you purchased. We have deliberately set our prices so low that no one |  |  |  | for the SARR/SALR is based on an appropriate graph or table from one of the references
can really claim that they can’t afford to pay. But low prices will work for us—that is, we |  |  |  | as shown on the worksheets.
can stay in business—only if we can sell enough copies. Bottom line: the more you get
other people to pay for their own copies, the more low-cost useful spreadsheets will be |  |  |  | The basin sizing calculations require values for several MBBR carrier properties: (specific
available for you in the future. |  |  |  | surface area in m2/m3 and % void space). Values to be used in the design calculations
should come from your carrier supplier.
This workbook is provided "as is", without warranty of any kind, express or
implied. |  |  |  | The aeration/blower calculations are made for a coarse bubble diffuser system.
Coarse bubble diffusers are typically used, because they work better
with the suspended carrier media.
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2018 Harlan H. Bengtson. All Rights Reserved.

## 2. Pre-Anoxic Denitrif.
MBBR Process Design Calculations - S.I. units
Pre-Anoxic Denitrification Process
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
I. Wastewater Parameter Inputs
1. Parameters for All Three Stages
Design ww Flow Rate, Qo = |  | 760 | m3/d |  | Prim. Effl. BOD, So = |  | 180 | mg/L
Prim. Effl. TKN Conc. = |  | 25 | mg/L |  | Prim. Effl. NO3-N Conc. = |  | 0 | mg/L
Peak Hour Factor = |  | 4 | Prim. Effl. Alkalinity = |  |  | 140 | mg/L as CaCO3 |  | Estimation of SARR/SALR Ratio: Default data points for derivation of a SARR vs SALR
equation are provided for The denitrification and BOD removal stages. They may be
2. Parameters for First (Pre-Anoxic) Stage: | [8 empty] | replaced by values from user data if such data is available. | [5 empty] | NOTE: This graph was prepared using values from a similar graph in
[5 empty] | Data points for SARR/SALR vs SALR | [9 empty] | Rusten and Paulsrud's presentation (Ref #6 below).
Target Effl. NO3-N Conc. = |  | 9 | mg/L |  | SALR (g/m2/d): |  | 0.2 | 0.5 |  | Typical Design Values for Carrier Surface Area Loading Rate (SALR):
Est. of NO3-N Recycle Rato: |  | 1.5228 |  |  | SARR/SALR: |  | 0.95 | 0.94 |  | (from References (2) below)
(QR/Qo) - An estimate is needed here to start |  |  |  | (default values above are from a graph of Pre-Anoxic
the iterative calculation in Sec IV below |  |  |  | SARR vs SALR in ref #6 below right)
Design Value of NO3-N Surface |  |  |  | (The graph is shown at the right.)
Area Loading Rate (SALR) = |  | 0.9 | g/m2/d |  | Slope, SARR/SALR vs SALR: |  |  | -0.033333
See information on typical design |  |  |  |  | Intercept, SARR/SALR vs SALR: |  |  | 0.95667
values for SALR at right. |  |  |  |  | Est. of SARR/SALR Rato = |  |  | 0.92667
|  |  |  | (Surf. Area Removal Rate/Surf. Area Loading Rate) | [9 empty] | Nitrification SARR:
3. Parameters for Second (BOD Removal) Stage:
Data points for SARR/SALR vs SALR
Design Value of BOD Surface |  |  |  |  | SALR (g/m2/d): |  | 7.5 | 15
Area Loading Rate (SALR) = |  | 6 | g/m2/d |  | SARR/SALR: |  | 0.925 | 0.875
See information on typical design |  |  |  | (default values above are from the table of typical values
values for SALR at right. |  |  |  | of % BOD removal vs SALR shown at the right from ref #2)
Est. of SARR/SALR Rato = |  | 0.935 |  |  | Slope, SARR/SALR vs SALR: |  |  | -0.0066667
(Surf. Area Removal Rate/Surf. Area Loading Rate) |  |  |  |  | Intercept, SARR/SALR vs SALR: |  |  | 0.975
4. Parameters for Third (Nitrification) Stage:
[9 empty] | Nitrification SARR: |  |  |  |  | Adapted from Metcalf & Eddy, 5th Ed, Fig 9-25
Min Design Temp., T = |  | 15 | oC | Target Effl NH4-N Conc, NH4-Ne = |  |  | 3.3 | mg/L | D.O. | SARRmax | N @ SARRmax
|  |  |  | Click on cell H26 and on arrow to select D.O Conc. |  |  |  |  | mg/L | g/m2/d | mg/L |  | The values in the table at the left come from Figure 9-25 in Metcalf & Eddy,
[5 empty] | D.O Conc. in Reactor = |  | 3 | mg/L | 2 | 0.61 | 0.5 |  | Wastewater Engineering, Treatment and Resource Recovery, 5th Ed.
5. Preliminary Calculations - Design SALR value for Nitrification | [8 empty] | 3 | 0.88 | 0.8 |  | The N values at SARRmax were read from Figure 9-25. The SARRmax
[9 empty] | 4 | 1.03 | 1 |  | values were calculated for those N values using Eqn 9-48 from Metcalf & Eddy,
% NH4-N removal = |  | 86.8% |  |  | NH4-Ne @ SARRmax = |  | 0.8 | mg/L | 5 | 1.23 | 1.3 |  | 5th Ed: SARR = [N/(2.2 + N)]*3.3, where N is the bulk liquid (effluent)
Maximum SARR = |  | 0.88 | g/m2/d | SARR @ NH4-Ne, 15oC, SARR15 = |  |  | 0.88 | g/m2/d | 6 | 1.41 | 1.65 |  | NH4-N concentration.
|  |  |  | SARR @ NH4-Ne, T oC, SARRT = |  |  | 0.88 | g/m2/d |  |  |  |  | SARR temperature correction coefficients being used are: q = 1.058 for DO limited
SARR Temp. Coeff, q = |  | 1.058 | Design Value for nitrification SALR = |  |  |  | 1.0138 | g/m2/d | 3 | 0.88 | 0.8 |  | conditions and q = 1.098 for ammonia limited conditions. (per Salvetti et al - see ref list below)
[13 empty] | SARR temperature adjustments are made with: | SARRT = SARR15q(T - 15)
II. Determine whether to use Pre-Anoxic or Post-Anoxic Denitrification
SALR is calculated as SARR/% removal.
Carbon:Nitrogen Ratio, C/N = |  | 7.2 |  | Use this Worksheet for Pre-Anoxic
Target % N removal = |  | 64% |  | Denitrification calculations |  |  |  |  | Criteria for Determining whether to use Pre- or Post-Denitrification:
(from references 1 and 2 below)
III. Carrier and Tank Shape Parameter Inputs for all Three Stages | [8 empty] | 1. Pre-Denitirication is suitable if C/N > 4 and Target % Removal of N < 75%
Carrier Spec. Surf. Area = |  | 500 | m2/m3 | Click on green box and then on |  |  |  |  | 2. Post-Denitirication should be used if C/N < 4 or Target % Removal of N > 75%
(from carrier mfr/vendor) |  |  |  | arrow to Select Tank Shape: |  |  | rectangular
Liquid Depth in Tank = |  | 2.4 | m |  | Carrier % Void Space = |  | 60%
Tank L:W ratio = |  | 1.5 |  |  | (from carrier mfr/vendor - only needed to
(target L:W - only used if tank is rectangular) |  |  |  |  | calculate hydraulic detention time)
IV. Calculation of Carrier Volume and Required Tank Volume & Dimensions
1. First Stage (Pre-Anoxic Tank) Calculations |  |  |  |  | (Carrier fill % is typically between 30% and 70%. Lower
values are more conservative, allowing future capacity
Design Carrier Fill % = |  | 40% | (for first stage) |  | expansion or reduction of SALR by adding more carrier.
NO3-N Daily Loading = |  | 10415.8273 | g/day |  | Calculated Tank Volume = |  | 57.8657 | m3 | Equations used for Tank Sizing - Pre-Anoxic Stage
Carrier Surf. Area needed = |  | 11573.1415 | m2 |  | Calculated Tank Width = |  | 4.0092 | m
Calculated Carrier Volume = |  | 23.1463 | m3 |  | Calculated Tank Length = |  | 6.0138 | m | NO3-N Daily Loading = Qo*Prim Effl NO3-N + Qo*NO3-N Recycle Ratio*Target Effl NO3-N
Tank Liquid Volume = |  | 48.6072 | m3 | Nominal Hydraulic Retention Time at |  |  |  |  | Carrier Surf. Area needed = Nitrate Daily Loading/SALR_PreAnoxic
[5 empty] | Design Average Flow = |  | 92.0978 | min | Carrier Volume needed = Carrier Surf Area/Carrier Spec Surf Area
Estimate of NO3-N Surface Area |  |  |  |  | Peak Hourly Flow = |  | 23.0245 | min | Required Tank Volume = Carrier Volume/Des Carrier Fill PerCent
Removal Rate, SARR = |  | 0.834 | g/m2/d | [5 empty] | Tank Width & Length calculated from: Tank Volume = L*W*Liquid Depth
Req'd NO3-N Removal Rate: |  | 9652 | g/day | Est. of NO3-N Removal Rate: |  |  | 9652 | g/day | Or, Tank Diameter calculated from: Tank Volume = (pD2/4)Liquid Depth
(for Effl. NO3-N = Target Value) |  |  |  | Est. Rem Rate - Req'd Rate: |  |  | 0 | g/day
Tank Liquid Volume = Tank Volume-((1-Carrier PerCent Void)*Carrier Volume)
NOTE: Use Excel's "Goal Seek" to find QR/Qo as follows: Place the cursor on cell H72 and click on | [8 empty] | Nominal HRT at Des Ave Flow = Tank Liq Vol/(WW Flow Rate/(24*60))
"Goal Seek" (in the "tools" menu of older versions and under "Data - What if Analysis" in newer | [8 empty] | Nominal HRT at Peak Hourly Flow = Hydr Det Time at Des Ave Flow/Peak Hour Factor
versions of Excel). Enter values to "Set cell:" H72, "To value:" 0, "By changing cell:" c17, and | [8 empty] | Estimated SARR = SALR(SARR/SALR)
click on "OK". The calculated value of QR/Qo will appear in cell C17 and cell H72 should equal zero | [8 empty] | Required NO3-N Removal Rate = Qo*(Prim Effl TKN - Effl N03-N - Effl NH3-N)
if the process worked properly. Note that an initial estimate of QR/Qo is needed in cell C17 to start | [8 empty] | Estimated NO3-N Removal Rate = SARR*Carrier Surf Area
the iterative process.
2. Second Stage (BOD Removal) Calculations
[5 empty] | Est. of Effl BOD Conc.: |  | 10.7858 | mg/L | Equations used for Tank Sizing - BOD Removal Stage
Design Carrier Fill % = |  | 72.76% | (for second stage)
BOD Daily Loading = |  | 126110.6467 | g/day |  | Calculated Tank Volume = |  | 57.7774 | m3 | BOD Daily Loading = (Qo*So) + (Qo*Recycle Rato*Se) - (0.67*(20/7)*NO3-N removal rate)
[5 empty] | Calculated Tank Width = |  | 4.0062 | m | Carrier Surf. Area needed = BOD Daily Loading/SALR_BOD
Carrier Surf. Area needed = |  | 21018.4411 | m2 |  | Calculated Tank Length = |  | 6.0092 | m | Carrier Volume needed, Required Tank Volume, and Tank dimensions
Calculated Carrier Volume = |  | 42.0369 | m3 | Nominal Hydraulic Retention Time at |  |  |  |  | use the same equations shown above.
Tank Liquid Volume = |  | 40.9627 | m3 |  | Design Average Flow = |  | 77.6135 | min
[5 empty] | Peak Hourly Flow = |  | 19.4034 | min | Tank Liquid Volume, Nominal HRTs, and Estimated SARR are
Estimate of BOD Surface Area |  |  |  | Calculated Effl BOD Conc.: |  |  | 10.7858 | mg/L | calculated as shown above.
Removal Rate, SARR = |  | 5.61 | g/m2/d |  | If the calculated Effl. BOD conc. Is too high, the |  |  |  | Estimated BOD Removal Rate = SARR*Carrier Surf Area
Est. of BOD Removal Rate: |  | 117913.4547 | g/day |  | design value of SALR (in cell C28) should be reduced. |  |  |  | Calculated Eff. BOD Conc. = (BOD Daily Loading - BOD Removal Rate)/Qo
|  |  | Estimated - Calculated Effl BOD Conc. = |  |  |  | 0 | mg/L
NOTE: Use Excel's "Goal Seek" to find BODe as follows: Place the cursor on cell H93 and click on
"Goal Seek" (in the "tools" menu of older versions and under "Data - What if Analysis" in newer | [8 empty] | Equations used for Tank Sizing - Nitrification Stage
versions of Excel). Enter values to "Set cell:" H93, "To value:" 0, "By changing cell:" H82, and
click on "OK". The calculated value of BODe will appear in cell H82 and cell H93 should equal zero | [8 empty] | NH3-N Daily Loading = Qo*Prim Effl NH3-N + Qo*Recycle Ratio*Effl NH3-N
if the process worked properly. Note that an initial estimate of BODe is needed in cell H82 to start | [8 empty] | Carrier Surf. Area needed = NH3-N Daily Loading/SALR_NH3-N
the iterative process. | [8 empty] | Carrier Volume needed, Required Tank Volume, and Tank dimensions
use the same equations shown above.
1st stage tank volume - 2nd stage tank volume = |  |  |  |  | 0.088279
To make the 2nd stage tank volume the same as the first stage tank volume, use | [8 empty] | Tank Liquid Volume, Nominal HRTs, and Estimated SARR are
Excel's Goal Seek process to set cell F101 equal to zero by changing the value in cell C83. | [8 empty] | calculated as shown above.
3. Third Stage (Nitrification) Calculations | [8 empty] | Estimated NH3-N Removal Rate = SARR*Carrier Surf Area
[5 empty] | Tank Liquid Volume = |  | 51.4909 | m3 | Calculated Eff. NH3-N Conc. = (NH3-N Daily Loading - NH3-N Removal Rate)/Qo
Design Carrier Fill % = |  | 64.77% | (for third stage) |  | Calculated Tank Volume = |  | 69.4972 | m3
NH3-N Daily Loading = |  | 22819.1367 | g/day
Carrier Surf. Area needed = |  | 22507.9666 | m2 |  | Calculated Tank Width = |  | 4.3937 | m | Rules of Thumb for Estimating Oxygen/Air Requirements - Coarse Bubble Diffusers:
Calculated Carrier Volume = |  | 45.0159 | m3 |  | Calculated Tank Length = |  | 6.5906 | m | Source:
Estimate of NH3-N Surface Area |  |  |  | Nominal Hydraulic Retention Time at |  |  |  |  | http://www.xylemwatersolutions.com/scs/sweden/sv-se/produkter/cirkulationspumpar/documents/san3.pdf
[5 empty] | Design Average Flow = |  | 97.5616 | min
1. The typical AOR/SOR (or AOTE/SOTE) is 0.50 for a coarse bubble aertion system.
1st stage tank volume - |  |  |  |  | Peak Hourly Flow = |  | 24.3904 | min |  |  |  | (or 0.33 for a fine bubble aeration system)
3rd stage tank volume = |  | -11.6315 | [6 empty] | 2. The typical SOTE is 2.5% per meter of diffuser submergence for a coarse bubble system
To make the 3rd stage tank volume the same as the first |  |  |  |  | Check on BOD SALR: |  | 0.36419 | g/m2/d |  |  | (or 6.6 % per meter of diffuser submergence for a fine bubble system)
stage tank volume, use Excel's Goal Seek process to set |  |  |  |  | (BOD SALR should be < 0.5 g/m2/d in order |  |  |  | 3. Air weighs 1.275 kg/m3 (at 0oC and 1 bar) and contains 23% oxygen by weight, thus:
cell C108 to zero by changing the value in cell C100. |  |  |  |  | to achieve a good nitrification rate)
V. Calculation of Oxygen/Air/Blower Requirements - BOD Removal Stage | [8 empty] | 4. Air contains 0.293 kg of oxygen/m3.
1. Inputs: (Values of "Rule of Thumb" Constants to be used in Calculations - See notes at right) | [8 empty] | 5. For biological treatment with SRT from 5 to 10 days, kg oxygen required /kg BOD removed
is typically in the range from 0.92 - 1.1 kg O2/kg BOD. Higher SRT results in a higher value
O2 needed per lb BOD = |  | 1.5 | kg O2/kg BOD |  | Depth of Diffusers = |  | 2.3 | m | of kg O2 required/kg BOD removed. (For a very high SRT, as is typical for an MBBR process,
O2 needed per lb NH3-N = |  | 4.57 | kg O2/kg NH3-N |  | Normal Temperature = |  | 0 | oC | this value would be about 1.5 kg O2/kg BOD removed.)
SOTE as Function of Depth = |  | 2.5% | % per m depth |  | Normal Pressure = |  | 1 | bar
AOTE/SOTE = |  | 0.5 |  |  | Atmospheric Pressure = |  | 1.014 | bar | 6. The oxidation of 1 kg of ammonia nitrogen typically requires 4.1 to 4.6 kg of oxygen.
Press. Drop across Diffuser = |  | 0.03 | bar |  | Air Density at STP = |  | 1.2 | kg/m3
(from mfr/vendor) |  |  |  |  | O2 Content in Air = |  | 0.277 | kg/m3
2. Second Stage (BOD Removal) Calculations:
Oxygen Requirement = |  | 189.166 | kg/day |  |  | AOTE = | 2.875% |  | Equations used for Oxygen/Air/Blower Calculations
| SOTE = | 5.75% |  |  | Air Requirement = |  | 989.7241 | Nm3/hr
Blower Outlet Pressure = |  | 1.2719 | bar absolute | [5 empty] | Oxygen Requirement (kg/day) = Qo(4.57(NH4-No - NH4-Ne)/(1000 g/kg)
VI. Calculation of Oxygen/Air/Blower Requirements - Nitrification Stage | [8 empty] | Pressure at Mid-Depth = Patm(100 kPa/bar) + [g4H2O(ddiff/2)]
AOTE = SOTE*a*F[(B(PD/Pstd)Cs - D.O.)/Css]q(tww - 20)
Inputs:
Std O2 transf effic, SOTE = |  | 5.6% |  |  | Des. Barom. Press., Patm = |  | 1.014 | bar
(from diffuser mfr or vendor) |  |  |  |  | (ambient pressue at site) |  |  |  | Nm3/hr = (kg/day O2/AOTE)*MWair/[O2 fract in air)(MWO2)(rair)(24 hr/day)]
Diffuser Fouling Factor, F = |  | 0.8 |  |  | Ratio of D.O. saturation in WW to that in clean
Ratio of oxygen transfer rate in wastewater |  |  |  |  | water at same T & P, B = |  | 1 |  | m3/hr = Nm3/hr[(Tww + 273.15)/(Tnorm + 273.15)](Pnorm/PB2)
to that in clean water, a = |  | 0.6 |  |  | Pressure drop across
Depth of diffuser, ddiff = |  | 2.5 | m |  | diffuser, DPdiff = |  | 0.021 | bar | PB2 = Patm + DPdiff(100 kPa/Bar) + gH2O*ddiff
Norm. Air Density, rair = |  | 1.275 | kg/m3 |  | (from diffuser mfr or vendor)
(at 0oC, 1 bar)
Calculations | [8 empty] | References for additional background information:
Oxygen Requirement = |  | 75.3684 | kg/day |  | Act O2 transf effic, AOTE = |  | 2.158% |  | 1. Odegaard, Hallvard, "Compact Wastewater Treatment with MBBR." DSD International Conference
Pressure at mid Depth, PD = |  | 113.6375 | kPa |  | Des. Air Flow Rate, Nm3/hr = |  | 494.2955 | Nm3/hr | Hong Kong, 12. 11-14-2014. |  |  |  | http://www.dsdic2014.hk/ppt/Presentation_(B4-1).pdf
D.O sat'n conc. for clean water at ww |  |  |  |  | Des. Air Flow Rate, m3/hr = |  | 407.4544 | m3/hr
temp. and 1 atm, Cs = |  | 10.0745 | mg/L | Blower Outlet Pressure, PB2 = |  |  | 1.2797 | bar | 2. Odegaard, H., "The Moving Bed Biofilm Reactor," in Igasrashi, T, Watanabe, Y., Asano, T. and
(Derivation of equation for sat'n D.O. vs T is shown on worksheet 4) | [8 empty] | Tambo, N., Water Environmental Engineering and Reuse of Water, Hokkaido Press 1999, p 250-305.
http://netedu.xauat.edu.cn/jpkc/netedu/jpkc2009/szylyybh/content/wlzy/7/3/The%20Moving%20Bed%20Biofilm%20Reactor.pdf
VII. Calculation of Alkalinity Requirements
3. Steichen & Phillips, H., M, Black & Veach, Process and Practical Design Considerations for
Input: | Target Effluent Alkalinity = |  |  |  | 80 | mg/L |  |  | IFAS and MBBR Technologies, Headworks International Presentation, 03/18/2010
http://www.headworksinternational.com/userfiles/file/Webinar/BV_Webinar_Slides.pdf
Constants needed for Calculations:
4. McQuarrie, J.P. and Boltz, J.P., Moving Bed Biofilm Reactor Technology: Process Applications,
Equiv Wt. of CaCO3 = |  | 50 | g/equiv. |  | Equiv Wt. of NaHCO3 = |  | 84 | g/equiv. | Design and Performance, Water Environment Research, Vol 83, No. 6. June 2011.
Alkalinity used for Nitrification = |  |  | 7.14 | g CaCO3/g NH3-N removed |  |  |  |  | 5. Bjornberg, Corey, "Moving Bed Biofilm Reactor for Nitrification/Denitrification"
Alkalinity produced by Denitrification = |  |  | 3.57 | g CaCO3/g NO3-N removed |  |  |  |  | https://www.ndsu.edu/pubweb/nrg/outreach/Moving%20Bed%20Biofilm%20Reactor%20for%20Denitrification%20Corey.pdf
Calculations | [8 empty] | 6. Rusten, B. and Paulsrud, B., Improved Nutrient Removal with Biofilm Reactors,
Aquateam - Norwegian Water Technology Center, Oslo, Norway.
Alkalinity to be added = |  |  | 37.818 | mg/L as CaCO3
Daily Alkalinity Requirement = |  |  | 28.7417 | kg/day as CaCO3 |  |  |  |  | 7. Metcalf & Eddy, "Wastewater Engineering Treatment and Resource Recovery", 5th Ed, McGraw-Hill, 2014
For sodium bicarbonate use to add alkalinity: | [8 empty] | 8. Salvetti, R., A. Azzellino, R. Canziani, and L. Bonomo (2006), "Effect of Temperature on Tertiary
Nitrification in Moving-Bed Biofilm Reactors," Water Res., 40, 15, 298-2993.
Daily NaHCO3 Requirement = |  |  | 48.286 | kg/day NaHCO3
[9 empty] | 9. Bengtson, Harlan H., |  | Spreadsheets for MBBR Denitrification Design Calculations,
an Amazon Kindle ebook.
Find more Excel spreadsheets for engineering at | [8 empty] | 10. Bengtson, Harlan H., |  | Spreadsheets for MBBR Process Design Calculations,
| EngineeringExcelTemplates.com | [7 empty] | available as a paperback book and as an Amazon Kindle ebook.
[9 empty] | 11. Bengtson, Harlan H., |  | Biological Wastewater Treatment Process Design Calculations
Copyright © 2018 Harlan H. Bengtson. All Rights Reserved. | [8 empty] | available as a paperback book and as an Amazon Kindle ebook.
cylindrical
rectangular
2
3
4
5
6

## 3. Post-Anoxic Denitrif
MBBR Process Design Calculations - S.I. units
Post-Anoxic Denitrification Process
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
I. Wastewater Parameter Inputs
1. Parameters for All Three Stages
Design ww Flow Rate, Qo = |  | 760 | m3/d |  | Prim. Effl. BOD, So = |  | 180 | mg/L
Prim. Effl. TKN Conc. = |  | 35 | mg/L |  | Prim. Effl. NO3-N Conc. = |  | 0 | mg/L | Estimation of SARR/SALR Ratio: Default data points for derivation of a SARR vs SALR
Peak Hour Factor = |  | 4 | Prim. Effl. Alkalinity = |  |  | 140 | mg/L as CaCO3 |  | equation are provided for The denitrification and BOD removal stages. They may be
replaced by values from user data if such data is available.
2. Parameters for First (BOD Removal) Stage:
[5 empty] | Data points for SARR/SALR vs SALR |  |  |  | Typical Design Values for Carrier Surface Loading Rate (SALR): |  |  |  |  | Nitrification SARR: ( adapted from Metcalf & Eddy, 5th Ed, Figure 9-25 )
Design Value of BOD Surface |  |  |  |  | SALR (g/m2/d): |  | 7.5 | 15 | (from Reference (2) below)
Area Loading Rate (SALR) = |  | 6 | g/m2/d |  | SARR/SALR: |  | 0.925 | 0.875
See information on typical design |  |  |  | (default values above are from the table of typical values
values for SALR at right. |  |  |  | of % BOD removal vs SALR shown at the right from ref #2)
Est. of SARR/SALR Rato = |  | 0.935 |  |  | Slope, SARR/SALR vs SALR: |  |  | -0.0066667
(Surf. Area Removal Rate/Surf. Area Loading Rate) |  |  |  |  | Intercept, SARR/SALR vs SALR: |  |  | 0.975
3. Parameters for Second (Nitrification) Stage:
Nitrification SARR:
Influent NH4-N Conc. = |  | 25 | mg/L | Target Effl NH4-N Conc, NH4-Ne = |  |  | 3.3 | mg/L | D.O. | SARRmax | N @ SARRmax
Min Design Temp., T = |  | 15 | oC | Click on cell H26 and on arrow to select D.O Conc. |  |  |  |  | mg/L | g/m2/d | mg/L |  | The values in the table at the left come from Figure 9-25 in Metcalf & Eddy,
[5 empty] | D.O Conc. in Reactor = |  | 3 | mg/L | 2 | 0.61 | 0.5 |  | Wastewater Engineering, Treatment and Resource Recovery, 5th Ed.
4. Preliminary Calculations - Design Nitrification SALR value | [8 empty] | 3 | 0.88 | 0.8 |  | The N values at SARRmax were read from Figure 9-25. The SARRmax
[9 empty] | 4 | 1.03 | 1 |  | values were calculated for those N values using Eqn 9-48 from Metcalf & Eddy,
% NH4-N removal = |  | 86.8% |  |  | NH4-Ne @ SARRmax = |  | 0.8 | mg/L | 5 | 1.23 | 1.3 |  | 5th Ed: SARR = [N/(2.2 + N)]*3.3, where N is the bulk liquid (effluent)
Maximum SARR = |  | 0.88 | g/m2/d | SARR @ NH4-Ne, 15oC, SARR15 = |  |  | 0.88 | g/m2/d | 6 | 1.41 | 1.65 |  | NH4-N concentration.
|  |  |  | SARR @ NH4-Ne, T oC, SARRT = |  |  | 0.88 | g/m2/d |  |  |  |  | SARR temperature correction coefficients being used are: q = 1.058 for DO limited
SARR Temp. Coeff, q = |  | 1.058 | Design Value for nitrification SALR = |  |  |  | 1.0138 | g/m2/d | 3 | 0.88 | 0.8 |  | conditions and q = 1.098 for ammonia limited conditions. (per Salvetti et al - see ref list below)
[13 empty] | SARR temperature adjustments are made with: |  | SARRT = SARR15q(T - 15)
5. Parameters for Third (Post-Anoxic) Stage:
[5 empty] | Data points for SARR/SALR vs SALR | [7 empty] | SALR is calculated as SARR/% removal.
Target Effl. NO3-N Conc. = |  | 4 | mg/L |  | SALR (g/m2/d): |  | 1 | 1.8
Design Value of BOD Surface |  |  |  |  | SARR/SALR: |  | 0.9 | 0.88889
Area Loading Rate (SALR) = |  | 2 | g/m2/d |  | (default values above are from a graph of
See information on typical design |  |  |  |  | Post-Anoxic SARR vs SALR in ref #6 below right)
values for SALR at right. |  |  |  |  | (The graph is shown at the right.)
Est. of SARR/SALR Rato = |  | 0.88611 |  |  | Slope, SARR/SALR vs SALR: |  |  | -0.013889
(Surf. Area Removal Rate/Surf. Area Loading Rate) |  |  |  |  | Intercept, SARR/SALR vs SALR: |  |  | 0.91389
II. Determine whether to use Pre-Anoxic or Post-Anoxic Denitrification
Carbon:Nitrogen Ratio, C/N = |  | 5.1429 |  | Use this Worksheet for Post-Anoxic
Target % N removal = |  | 88.57% |  | Denitrification calculations |  |  |  |  | NOTE: This graph was prepared using values from a similar graph in
Rusten and Paulsrud's presentation (Ref #6 below).
III. Carrier and Tank Shape Parameter Inputs for all Three Stages
Criteria for Determining whether to use Pre- or Post-Denitrification:
Carrier Spec. Surf. Area = |  | 500 | m2/m3 | Click on green box and then on |  |  |  |  | (from references 1 and 2 below)
(from carrier mfr/vendor) |  |  |  | arrow to Select Tank Shape: |  |  | rectangular
Liquid Depth in Tank = |  | 2.4 | m |  | Carrier % Void Space = |  | 60% |  | 1. Pre-Denitirication is suitable if C/N > 4 and Target % Removal of N < 75%
Tank L:W ratio = |  | 1.5 |  |  | (from carrier mfr/vendor - only needed to
(target L:W - only used if tank is rectangular) |  |  |  |  | calculate hydraulic detention time) |  |  |  | 2. Post-Denitirication should be used if C/N < 4 or Target % Removal of N > 75%
IV. Calculation of Carrier Volume and Required Tank Volume & Dimensions | [8 empty] | Equations used for Tank Sizing - BOD Removal Stage
1. First Stage (BOD Removal) Calculations |  |  |  |  | (Carrier fill % is typically between 30% and 70%. Lower |  |  |  | BOD Daily Loading = (Qo*So)
[5 empty] | values are more conservative, allowing future capacity |  |  |  | Carrier Surf. Area needed = BOD Daily Loading/SALR_BOD
Design Carrier Fill % = |  | 60% | (for first stage) |  | expansion or reduction of SALR by adding more carrier. |  |  |  | Carrier Volume needed = Carrier Surf Area/Carrier Spec Surf Area
BOD Daily Loading = |  | 136800 | g/day | [5 empty] | Required Tank Volume = Carrier Volume/Des Carrier Fill PerCent
[5 empty] | Required Tank Volume = |  | 76 | m3 | Tank Width & Length calculated from: Tank Volume = L*W*Liquid Depth
Carrier Surf. Area needed = |  | 22800 | m2 |  | Calculated Tank Width = |  | 4.5947 | m | Or, Tank Diameter calculated from: Tank Volume = (pD2/4)Liquid Depth
Calculated Carrier Volume = |  | 45.6 | m3 |  | Calculated Tank Length = |  | 6.892 | m
Tank Liquid Volume = |  | 57.76 | m3 | Nominal Hydraulic Retention Time at |  |  |  |  | Tank Liquid Volume = Tank Volume-((1-Carrier PerCent Void)*Carrier Volume)
[5 empty] | Design Average Flow = |  | 109.44 | min | Nominal HRT at Des Ave Flow = Tank Liq Vol/(WW Flow Rate/(24*60))
Estimate of BOD Surface Area |  |  |  |  | Peak Hourly Flow = |  | 27.36 | min | Nominal HRT at Peak Hourly Flow = Hydr Det Time at Des Ave Flow/Peak Hour Factor
Removal Rate, SARR = |  | 5.61 | g/m2/d | Calculated Effl BOD Conc.: |  |  | 11.7 | mg/L | Estimated SARR = SALR(SARR/SALR)
Est. of BOD Removal Rate: |  | 127908 | g/day |  | If the calculated Effl. BOD conc. Is too high, the |  |  |  | Estimated BOD Removal Rate = SARR*Carrier Surf Area
[5 empty] | design value of SALR (in cell C17) should be reduced. |  |  |  | Calculated Eff. BOD Conc. = (BOD Daily Loading - BOD Removal Rate)/Qo
2. Second Stage (Nitrification) Calculations | [8 empty] | Equations used for Tank Sizing - Nitrification Stage
Design Carrier Fill % = |  | 70% | (for second stage) Tank Liquid Volume = |  |  |  | 53.9746 | m3 | NH3-N Daily Loading = Qo*Prim Effl NH3-N
NH3-N Daily Loading = |  | 26600 | g/day |  | Required Tank Volume = |  | 74.9644 | m3 | Carrier Surf. Area needed = NH3-N Daily Loading/SALR_NH3-N
[5 empty] | Calculated Tank Width = |  | 4.5633 | m | Carrier Volume needed, Required Tank Volume, and Tank dimensions
Carrier Surf. Area needed = |  | 26237.2727 | m2 |  | Calculated Tank Length = |  | 6.8449 | m | use the same equations shown above.
Calculated Carrier Volume = |  | 52.4745 | m3
|  |  |  | Nominal Hydraulic Retention Time at |  |  |  |  | Tank Liquid Volume, Nominal HRTs, and Estimated SARR are
1st stage tank volume - |  |  |  |  | Design Average Flow = |  | 102.2677 | min | calculated as shown above.
- 2nd stage tank volume = |  | 1.0356 |  |  | Peak Hourly Flow = |  | 25.5669 | min | Estimated NH3-N Removal Rate = SARR*Carrier Surf Area
To make the 2nd stage tank volume the same as the | [8 empty] | Calculated Eff. NH3-N Conc. = (NH3-N Daily Loading - NH3-N Removal Rate)/Qo
first stage, use Excel's Goal Seek process to set cell |  |  |  |  | Check on BOD SALR: |  | 0.33891 | g/m2/d
C83 equal to zero by changing the value in cell C76. |  |  |  |  | (BOD SALR should be < 0.5 g/m2/d in order
to achieve a good nitrification rate)
3. Third Stage (Post-Anoxic) Calculations | [8 empty] | Equations used for Tank Sizing - Post-Anoxic Stage
Design Carrier Fill % = |  | 31.7% | (for third stage) Required Tank Volume = |  |  |  | 76 | m3 | NO3-N Daily Loading = Qo*Prim Effl NO3-N
NO3-N Daily Loading = |  | 24092 | g/day |  | Calculated Tank Width = |  | 4.5947 | m | Carrier Surf. Area needed = Nitrate Daily Loading/SALR_PreAnoxic
Carrier Surf. Area needed = |  | 12046 | m2 |  | Calculated Tank Length = |  | 6.892 | m | Carrier Volume needed, Required Tank Volume, and Tank dimensions
Calculated Carrier Volume = |  | 24.092 | m3 | Nominal Hydraulic Retention Time at |  |  |  |  | use the same equations shown above.
Tank Liquid Volume = |  | 66.3632 | m3 |  | Design Average Flow = |  | 125.7408 | min
Estimate of NO3-N Surface Area |  |  |  |  | Peak Hourly Flow = |  | 31.4352 | min | Tank Liquid Volume, Nominal HRTs, and Estimated SARR are
Removal Rate, SARR = |  | 1.7722 | g/m2/d | Calculated Effl NO3-N Conc.: |  |  | 3.6103 | mg/L | calculated as shown above.
Est. of NO3-N Removal Rate: |  | 21348.1889 | g/day |  | If the calculated Effl. NO3-N conc. Is |  |  |  | Required NO3-N Removal Rate = Qo*(Prim Effl TKN - Effl N03-N - Effl NH3-N)
1st stage tank volume - |  |  |  |  | too high, the design value of SALR |  |  |  | Estimated NO3-N Removal Rate = SARR*Carrier Surf Area
3rd stage tank volume = |  | -3.6056e-06 |  |  | (in cell C36) should be reduced. |  |  |  | Calculated Eff. NO3-N Conc. = (NO3-N Daily Loading - NO3-N Removal Rate)/Qo
To make the 3rd stage tank volume the same as the first
stage tank volume, use Excel's Goal Seek process to set
cell C99 equal to zero by changing the value in cell C90. | [8 empty] | Rules of Thumb for Estimating Oxygen/Air Requirements - Coarse Bubble Diffusers:
Source:
V. Calculation of Oxygen/Air/Blower Requirements - BOD Removal Stage | [8 empty] | http://www.xylemwatersolutions.com/scs/sweden/sv-se/produkter/cirkulationspumpar/documents/san3.pdf
1. Inputs: (Values of "Rule of Thumb" Constants to be used in Calculations - See notes at right) | [8 empty] | 1. The typical AOR/SOR (or AOTE/SOTE) is 0.50 for a coarse bubble aertion system.
(or 0.33 for a fine bubble aeration system)
O2 needed per kg BOD = |  | 1.5 | kg O2/kg BOD |  | Depth of Diffusers = |  | 2.3 | m | 2. The typical SOTE is 2.5% per meter of diffuser submergence for a coarse bubble system
O2 needed per lb NH3-N = |  | 4.57 | kg O2/kg NH3-N |  | Normal Temperature = |  | 0 | oC |  |  | (or 6.6 % per meter of diffuser submergence for a fine bubble system)
SOTE as Function of Depth = |  | 2.5% | % per m depth |  | Normal Pressure = |  | 1 | bar | 3. Air weighs 1.275 kg/m3 (at 0oC and 1 bar) and contains 23% oxygen by weight, thus:
AOTE/SOTE = |  | 0.5 |  |  | Atmospheric Pressure = |  | 1.014 | bar
Press. Drop across Diffuser = |  | 0.03 | bar |  | Air Density at STP = |  | 1.2 | kg/m3 | 4. Air contains 0.293 kg of oxygen/m3.
(from mfr/vendor) |  |  |  |  | O2 Content in Air = |  | 0.277 | kg/m3
5. For biological treatment with SRT from 5 to 10 days, kg oxygen required /kg BOD removed
2. First Stage (BOD Removal) Calculations: | [8 empty] | is typically in the range from 0.92 - 1.1 kg O2/kg BOD. Higher SRT results in a higher value
of kg O2 required/kg BOD removed. (For a very high SRT, as is typical for an MBBR process,
Oxygen Requirement = |  | 205.2 | kg/day |  |  | AOTE = | 2.875% |  | this value would be about 1.5 kg O2/kg BOD removed.)
| SOTE = | 5.75% |  |  | Air Requirement = |  | 1073.6148 | Nm3/hr
Blower Outlet Pressure = |  | 1.2696 | bar absolute | [5 empty] | 6. The oxidation of 1 kg of ammonia nitrogen typically requires 4.1 to 4.6 kg of oxygen.
VI. Calculation of Oxygen/Air/Blower Requirements - Nitrification Stage
References for additional background information:
Inputs:
Std O2 transf effic, SOTE = |  | 5.6% |  |  | Des. Barom. Press., Patm = |  | 1.014 | bar | 1. Odegaard, Hallvard, "Compact Wastewater Treatment with MBBR." DSD International Conference
(from diffuser mfr or vendor) |  |  |  |  | (ambient pressue at site) |  |  |  | Hong Kong, 12. 11-14-2014. |  |  |  | http://www.dsdic2014.hk/ppt/Presentation_(B4-1).pdf
Diffuser Fouling Factor, F = |  | 0.8 |  |  | Ratio of D.O. saturation in WW to that in clean
Ratio of oxygen transfer rate in wastewater |  |  |  |  | water at same T & P, B = |  | 1 |  | 2. Odegaard, H., "The Moving Bed Biofilm Reactor," in Igasrashi, T, Watanabe, Y., Asano, T. and
to that in clean water, a = |  | 0.6 |  |  | Pressure drop across |  |  |  | Tambo, N., Water Environmental Engineering and Reuse of Water, Hokkaido Press 1999, p 250-305.
Depth of diffuser, ddiff = |  | 2.5 | m |  | diffuser, DPdiff = |  | 0.021 | bar | http://netedu.xauat.edu.cn/jpkc/netedu/jpkc2009/szylyybh/content/wlzy/7/3/The%20Moving%20Bed%20Biofilm%20Reactor.pdf
Std. Air Density, rair = |  | 1.2 | kg/m3 |  | (from diffuser mfr or vendor)
(at 0oC, 1 bar) | [8 empty] | 3. Steichen & Phillips, H., M, Black & Veach, Process and Practical Design Considerations for
Calculations | [8 empty] | IFAS and MBBR Technologies, Headworks International Presentation, 03/18/2010
http://www.headworksinternational.com/userfiles/file/Webinar/BV_Webinar_Slides.pdf
Oxygen Requirement = |  | 75.3684 | kg/day |  | Act O2 transf effic, AOTE = |  | 1.914%
Pressure at mid Depth, PD = |  | 113.6375 | kPa |  | Des. Air Flow Rate, Nm3/hr = |  | 592.3767 | Nm3/hr | 4. McQuarrie, J.P. and Boltz, J.P., Moving Bed Biofilm Reactor Technology: Process Applications,
D.O sat'n conc. for clean water at ww |  |  |  |  | Des. Air Flow Rate, m3/hr = |  | 488.304 | m3/hr | Design and Performance, Water Environment Research, Vol 83, No. 6. June 2011.
temp. and 1 atm, Cs = |  | 10.0745 | mg/L | Blower Outlet Pressure, PB2 = |  |  | 1.2797 | bar
(Derivation of equation for sat'n D.O. vs T is shown on worksheet 4) | [8 empty] | 5. Bjornberg, Corey, "Moving Bed Biofilm Reactor for Nitrification/Denitrification"
https://www.ndsu.edu/pubweb/nrg/outreach/Moving%20Bed%20Biofilm%20Reactor%20for%20Denitrification%20Corey.pdf
VII. Calculation of Alkalinity Requirements | [8 empty] | 6. Rusten, B. and Paulsrud, B., Improved Nutrient Removal with Biofilm Reactors,
Aquateam - Norwegian Water Technology Center, Oslo, Norway.
Input: | Target Effluent Alkalinity = |  |  |  | 80 | mg/L
Constants needed for Calculations: | [8 empty] | Source for information about Carbon Sources for Denitrification and Required Dosages:
https://www.werf.org/c/KnowledgeAreas/NutrientRemoval/compendium/05-Tertiary_Denitrification_Processes.aspx
Equiv Wt. of CaCO3 = |  | 50 | g/equiv. |  | Equiv Wt. of NaHCO3 = |  | 84 | g/equiv.
Alkalinity used for Nitrification = |  |  | 7.14 | g CaCO3/g NH3-N removed
Alkalinity produced by Denitrification = |  |  | 3.57 | g CaCO3/g NO3-N removed |  |  |  |  | Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Calculations
Alkalinity to be added = |  |  | 54.2767 | mg/L as CaCO3 |  |  |  |  | Copyright © 2018 Engineering Excel Templates. All Rights Reserved.
Daily Alkalinity Requirement = |  |  | 41.2503 | kg/day as CaCO3
For sodium bicarbonate use to add alkalinity:
Daily NaHCO3 Requirement = |  |  | 69.3005 | kg/day NaHCO3
VII. Calculation of Carbon Source Requirements
Inputs: | Carbon Source to be used: |  |  |  | Methanol
| COD Requirement for Denitrification = |  |  |  | 4.6 | kg COD/kg NO3-N removed
| COD Content of Carbon Source = |  |  |  | 1.5 | kg COD/kg Carbon Source
Calculations
Carbon Source Dosage = |  |  | 3.0667 | kg Carbon Source/kg NO3-N removed
Daily Carbon Source Requirement = |  |  | 73.8821 | kg/day
cylindrical
rectangular
2
3
4
5
6

## 4. Satn DO vs T
Derivation of Equation for Saturation DO Concentration at WW Temperature:
Sat'n DO
T, oC | mg/L
0 | 14.62
1 | 14.22
2 | 13.83
3 | 13.46
4 | 13.11
5 | 12.77
6 | 12.45
7 | 12.14
8 | 11.84
9 | 11.56
10 | 11.29
11 | 11.03
12 | 10.78
13 | 10.54
14 | 10.3
15 | 10.08
16 | 9.87
17 | 9.66 | Source for DO vs T data: USGS website at:
18 | 9.47
19 | 9.28 |  | http://water.usgs.gov/software/DOTABLES/
20 | 9.09
21 | 8.92
22 | 8.74
23 | 8.58
24 | 8.42
25 | 8.26
26 | 8.11
27 | 7.97
28 | 7.83
29 | 7.69
30 | 7.56
31 | 7.43
32 | 7.3
33 | 7.18
34 | 7.06
35 | 6.95