## 1. Contents
Workbook Contents
Click on tabs at the bottom of the screen to access the following:
Tab 1. Contents (current tab)
Tab 2. Horiz. Flow Grit Chamber Design
Tab 3. Estimation of Peaking Factor
Why you shouldn’t give copies of this workbook away
We at EngineeringExcelTemplates.com hope that you find this workbook useful. If you
would like us to develop additional useful spreadsheets for you in the future, then encourage
your friends and colleagues to buy their own copies, rather than allowing them to copy
the spreadsheet you purchased. We have deliberately set our prices so low that no one
can really claim that they can’t afford to pay. But low prices will work for us—that is, we
can stay in business—only if we can sell enough copies. Bottom line: the more you get
other people to pay for their own copies, the more low-cost useful spreadsheets will be
available for you in the future.
This workbook is provided "as is", without warranty of any kind, express or
implied.
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2014 Engineering Excel Templates. All Rights Reserved.

## 2. Horiz Flow Grit Chamber Des
Horiz. Flow Grit Chamber Design Calculations - S.I. units
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes | [6 empty] | Typical Values for Horizontal Flow Grit Chamber Design Parameters
Inputs | [6 empty] | Parameter | Units | Range | Typical Value
Design Ave Flow Rate, Q = |  | 10500 | m3/d | Design Horiz. Velocity, V = | 0.3 | m/s | Detention Time | seconds | 45 - 90 | 60
Peaking Factor, PF = |  | 2.51 |  | Design Detention Time ,t = | 60 | sec | Horizontal Velocity | m/s | 0.25 - 0.4 | 0.3
(Peak hourly flow/Average Flow) |  |  |  | Per Cent Additional |  |  | Added Length for
No. of Tanks in Parallel, N = |  | 2 |  | length for Inlet and Outlet = | 25% |  | Inlet and Outlet | % | 25 - 50 | 30
Tank Freeboard, DFB= |  | 0.3 | m | Depth for Grit Storage, DGR= | 0.25 | m | The values in the table above are from Table 5-16 in
Metcalf & Eddy, Wastewater Engineering Treatment and Resource
Calculations | [6 empty] | Recovery, 5th Ed., 2014
Peak Hourly Flow Rate, Qp = |  | 26355 | m3/d | Length for Flow , Lf = | 18 | m | NOTE: The next worksheet may be used to estimate the peaking
|  |  |  | Cross-Sectional |  |  | factor based on the design average flow rate. If you use that
Grit Chamber Volume, V = |  | 18.3021 | m3 | Area of Flow, A = | 1.0168 | m2 | worksheet, enter the result in cell C9 above left.
(for each tank)
Tank Width, W = |  | 1 | m | Depth of Fow, D = | 1.0168 | m
(User input for value of A above right)
Tank Length, L = |  | 22.5 | m | Tank Wall Depth, DW = | 1.5668 | m
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2020 Harlan H. Bengtson. All Rights Reserved.

## 3. Est. of Peaking Factor
Estimation of Peaking Factor - S.I. units
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes | [5 empty] | NOTE: The peaking factor is calculated from the following equation:
Inputs |  |  |  | Calculations
where P is the population in thousands
Design Ave Flow Rate, Q = |  | 10500 | m3/d | Peaking Factor, PF = | 2.5108
(Peak hourly flow/Average Flow)
A factor of 3.785 m3/capita for daily ave. flow rate, or 3785 m3/thousand in population was used
to calculate PF for a specified value of Design Daily Average Flow Rate.
| Find more Excel spreadsheets for engineering at |  |  |  |  | SOURCE: This equation is from Page 10-6 of the publication, Recommended Standards
|  | EngineeringExcelTemplates.com |  |  |  |  | for Wastewater Treatment Facilities, 2014, commonly referred to as
the "10 States Standards"
| Copyright © 2020 Harlan H. Bengtson. All Rights Reserved. | [5 empty] | This publication is available for download from the following web address:
https://www.health.state.mn.us/communities/environment/water/tenstates/standards.html